# Bug 17

| Summary: | The value entered for Trained oscillator base value is not displayed in LQ |  |  |
| --- | --- | --- | --- |
| Product: | QNet_R2 | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | MCOM | Assignee: | Grant Irani <girani@qualitrolcorp.com> |
| Status: | IN_PROGRESS --- |  |  |
| Severity: | minor | CC: | dplatten@qualitrolcorp.com, pfrench@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-10-29 08:55:08 EDT Value shown in LQ is current Trained Oscillator Correction. Should we also display the Trained Oscillator Base Value used at startup? MC>LQ<cr> List QNet Configuration Station name: QNET4100 Station number: 25 Scanners enabled: 1..4 Base point: 1 Max point: 256 Local time zone: America/UnitedStates/New_York Precision time source: IRIG TTL IEEE UTC Trained oscillator correction: 303 High stability oscillator: No PPS on fiber: No NTP Servers: 10.75.2.45 Event indent: Alarm Separate return legends: Yes Hourly time print: Yes Minute for hourly time print: 0 Alarm summary at midnight: No Alarm summary on reset: No Clear historical buffer on reboot: No Time sorted port groups: 24 List QNet Configuration complete MC> GI - Add separate value for setting vs actual: Trained oscillator correction base value: xxxx <<<<<<<<<<< Trained oscillator correction current value: 303 <<<<<<<<<<< MC>LQ<cr> List QNet Configuration Station name: QNET4100 Station number: 25 Scanners enabled: 1..4 Base point: 1 Max point: 256 Local time zone: America/UnitedStates/New_York Precision time source: IRIG TTL IEEE UTC Trained oscillator correction base value: 269 Trained oscillator correction current value: 303 High stability oscillator: No PPS on fiber: No NTP Servers: 10.75.2.45 Event indent: Alarm Separate return legends: Yes Hourly time print: Yes Minute for hourly time print: 0 Alarm summary at midnight: No Alarm summary on reset: No Clear historical buffer on reboot: No Time sorted port groups: 24 List QNet Configuration complete MC> DP - Need retest in Next Version code modified to match comments section above. Comment 1 David Platten 2013-10-29 08:56:14 EDT old ID 52 Comment 2 David Platten 2013-10-29 14:43:29 EDT not fixed. i'm expecting to see a new value for: Trained oscillator correction base value, and i don't see it in version 2.2.2d. 29 Oct 2013 18:37:08 c LC>LQ List QNet Configuration Station name: QNet4100 Station number: 1 Scanners enabled: 1 Base point: 1 Max point: 64 Local time zone: America/UnitedStates/New_York Precision time source: None Trained oscillator correction: 0 High stability oscillator: No PPS on fiber: No NTP Servers: None Event indent: Alarm Separate return legends: Yes Hourly time print: Yes Minute for hourly time print: 0 Alarm summary at midnight: No Alarm summary on reset: No Clear historical buffer on reboot: No Time sorted port groups: None List QNet Configuration complete LC> Comment 3 Peter French 2013-11-12 10:24:06 EST This does appear to be incorporated in 2.2.3: LC>LQ List QNet Configuration Station name: QNet4100 Station number: 1 Scanners enabled: 1 Base point: 1 Max point: 64 Local time zone: America/UnitedStates/New_York Precision time source: IRIG TTL NoYear UTC Trained oscillator correction base balue: 0 <<<<<< Trained oscillator correction current value: 0 <<<<<< High stability oscillator: No PPS on fiber: No NTP Servers: None Event indent: Alarm Separate return legends: Yes Hourly time print: Yes Minute for hourly time print: 0 Alarm summary at midnight: No Alarm summary on reset: No Clear historical buffer on reboot: No Time sorted port groups: None List QNet Configuration complete LC> Need to migrate to 2.2.2 patch |  |
| --- | --- |

# Bug 32

| Summary: | BPA commands 23, 24, 25, 26, 27, 28, 29 and 2A are not working correctly. |  |  |
| --- | --- | --- | --- |
| Product: | QNet_R2 | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | BPA | Assignee: | Grant Irani <girani@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | minor | CC: | dplatten@qualitrolcorp.com, pfrench@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-10-29 09:50:36 EDT BPA commands 23, 24, 25, 26, 27, 28, 29 and 2A are not working correctly. Executing these commands in the bpaconsole test tool hangs the test application. Need to update XML for partial downoads. Need a better test tool! DP - Please retest in next with next release. See also new BPA test console tool!!! BPAConsole tool used wrong buffer for LRC check. Partial XML commands are obsolete, and now return CAN. old id 353 Comment 1 David Platten 2013-11-05 09:59:05 EST ready for test. Comment 2 David Platten 2013-11-07 15:36:49 EST Not sure if these are working as designed or not. Previous dev comments state they should be returning CAN but instead they are opening an "Open" file dialog box, as if to send a file, but most of these commands I'm guessing are to save configuration files so i would expect a "Save As" dialog box to save the config xml. used Grant's BPAConsole test tool dated 7/16/2013 for this test. verified not working as expected in 2.2.2d. Comment 3 David Platten 2013-11-12 08:50:58 EST assigning to Grant. Comment 4 David Platten 2013-12-05 09:22:17 EST changing to minor. Grant, please confirm that this is a test tool issue. |  |
| --- | --- |

# Bug 143

| Summary: | 61850 server failed to initialize SCL configuration |  |  |
| --- | --- | --- | --- |
| Product: | QNet_R2 | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | IEC61850 | Assignee: | Grant Irani <girani@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | dplatten@qualitrolcorp.com, pfrench@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | 2.2.3 |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-11-19 15:26:24 EST 61850 server failed to initialize SCL configuration Cannot connect to the QNet controller with the IECBrowser after creating a 61850 port. TELNET INFO: ******************************************* # ls -al drwxrwxrwx 2 1543 1543 1024 Nov 19 15:20 . drwxr-xr-x 16 root root 1024 Nov 19 15:09 .. srwxr-xr-x 1 root root 0 Nov 19 15:10 fastnotify_ifc -------r-- 1 root root 1324 Nov 19 15:10 i850server.out -rw-r--r-- 1 root root 4 Nov 19 15:09 lighttpd.pid -rw-r--r-- 1 root root 0 Nov 19 15:09 ntpscript srwxr-xr-x 1 root root 0 Nov 19 15:10 scan934 srwxrwxrwx 1 root root 0 Nov 19 15:10 scanifc -rw-r--r-- 1 root root 4 Nov 19 15:20 xinetd.pid # cat i850* sh: can't create /proc/sys/net/ipv6/tcp_keepalive_time: nonexistent directory sh: can't create /proc/sys/net/ipv6/tcp_keepalive_intvl: nonexistent directory sh: can't create /proc/sys/net/ipv6/tcp_keepalive_probes: nonexistent directory mkdir: can't create directory '/dd/files': File exists Segmentation fault SCL Version: 2003:A In DA(d) near line 6862: Warning - member d not found in RTG class DPL In DA(d) near line 6862: Warning: Using default SCL type for LPHD1$DC$PhyNam$d In DA(d) near line 6862: Warning - member d not found in RTG class DPL In DA(d) near line 6862: Warning: Using default SCL type for LPHD1$DC$PhyNam$d In DA(d) near line 6862: Warning - member d not found in RTG class DPL In DA(d) near line 6862: Warning: Using default SCL type for LPHD1$DC$PhyNam$d In DA(d) near line 6862: Warning - member d not found in RTG class DPL In DA(d) near line 6862: Warning: Using default SCL type for GGIO1$DC$EEName$d In DA(d) near line 6862: Warning - member d not found in RTG class DPL In DA(d) near line 6862: Warning: Using default SCL type for GGIO1$DC$EEName$d In DA(d) near line 6862: Warning - member d not found in RTG class DPL In DA(d) near line 6862: Warning: Using default SCL type for GGIO1$DC$EEName$d Dictionary error: Duplicate name Failed to initialize SCL configuration: /r1/files/QNet.cid # STEPS TO REPRODUCE: ********************************************** >mc QNet4100 Station number: 1 19 Nov 2013 20:08:34 Enter password: **** MC>MP Modify Ports sub menu MP>MP Modify Port Configuration Port name? my61850port Create a new port (Y,N)? y Protocol? [none]? Available protocols: none console printer colorprint CRT BPA data annunciator DNP 61850 60870 Modbu s Protocol? [none]61850 Setting protocol to: 61850 Edition (1,2)? [1] Use weak security (Y,N)? [N] DataSet name? GOOSE adapter (eth0, eth1)? [eth0] GOOSE subscription name? GOOSE control block name? Port name? Modify Port Configuration complete MP> Leave MP and return to MC menu (Y,N)? y Modify Ports sub menu complete MC>lp List Port Configuration Port group unassigned: my61850port: IEC 61850 Edition: 1 Security: None Defined Datasets No DataSets are defined GOOSE adapter eth0 GOOSE subscriptions No GOOSE subscriptions are defined GOOSE output Control Blocks No GOOSE publish blocks are defined Port group 1: Port0: console Serial port 0, 38400, 8-N-1, UTC netcon: console, Network port 21000, Local List Port Configuration complete MC> Configuration has been modified. WARNING: System will reboot after changes are saved Save, Restore, or Continue (S,R,C)? s Saving configuration... Rebooting to load new configuration... €x€x€x€x€x€x€x€x€x€x€x€x€x€x€x€x€x€x€x€x€x QNET 4100 version 2.2.3 release Aug 21 2013 System down 19 Nov 2013 20:09:40 System up 19 Nov 2013 20:10:00 QNet4100 is Primary controller > A 20:09:40.001 #D 1 System Down A 20:09:56.615 #G 1 System Fail Alarm N 20:10:05.655 #D 1 System Up N 20:10:05.655 #G 1 System Fail Normal A 20:13:01.003 #D 19 Network port Failure N 20:14:01.001 #D 19 Network port Normal >lc QNet4100 Station number: 1 19 Nov 2013 20:17:31 LC>lp List Port Configuration Port group unassigned: my61850port: IEC 61850 Edition: 1 Security: None Defined Datasets No DataSets are defined GOOSE adapter eth0 GOOSE subscriptions No GOOSE subscriptions are defined GOOSE output Control Blocks No GOOSE publish blocks are defined Port group 1: Port0: console Serial port 0, 38400, 8-N-1, UTC netcon: console, Network port 21000, Local List Port Configuration complete LC> |  |
| --- | --- |

# Bug 115

| Summary: | "....: Software caused connection abort: recv failed" after trying to upload config file to QNet controller using QCA app. |  |  |
| --- | --- | --- | --- |
| Product: | QNet_R2 | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | Java (QCA) | Assignee: | Grant Irani <girani@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | dplatten@qualitrolcorp.com, girani@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | 2.2.2d |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |
| Attachments: | pic 1 |  |  |

| Description David Platten 2013-11-14 12:09:10 EST Created attachment 8 [details] pic 1 "....: Software caused connection abort: recv failed" after trying to upload config file to QNet controller using QCA app. This happened after falling into a slightly different endless loop that the previous endless loop bug, and iterating through it a few times. refer to attached screenshot. |  |
| --- | --- |

# Bug 116

| Summary: | QCA > Time > Precision time source > PPM > No error flagged for a Scanner point number greater than the max scanner point. |  |  |
| --- | --- | --- | --- |
| Product: | QNet_R2 | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | Java (QCA) | Assignee: | Grant Irani <girani@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | dplatten@qualitrolcorp.com, girani@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | 2.2.2d |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-11-14 16:47:49 EST QCA > Time > Precision time source > PPM > No error flagged for a Scanner point number greater than the max scanner point. range of points is 1 to 192. entered point 220 and the text is highlighted green for a change but it should be highlighted red to indicate an error. It is supposed to within the range of valid scanner points. |  |
| --- | --- |

# Bug 21

| Summary: | The file operation information dialog box is blank sometimes. |  |  |
| --- | --- | --- | --- |
| Product: | QNet_R2 | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | Java (QCA) | Assignee: | Grant Irani <girani@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | minor | CC: | dplatten@qualitrolcorp.com, girani@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-10-29 09:27:41 EDT Dialog box(es) do not always paint correctly. See attachment: The file operation information dialog box is sometimes blank or takes other display background content. |  |
| --- | --- |

# Bug 138

| Summary: | QCA > Port > able to add, save and upload a port that uses the default protocol selection "unused". |  |  |
| --- | --- | --- | --- |
| Product: | QNet_R2 | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | Java (QCA) | Assignee: | Grant Irani <girani@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | dplatten@qualitrolcorp.com, girani@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | 2.2.3 |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-11-18 15:58:58 EST QCA > Port > able to add, save and upload a port that uses the default protocol selection "unused". i.e. >lc QNet4100 Station number: 1 18 Nov 2013 20:59:54 LC>lp List Port Configuration Port group 1: Port0: console Serial port 0, 38400, 8-N-1, UTC netcon: console, Network port 21000, Local PortDef2: unused Serial port 2, 9600, 8-N-1 Need to add protocol display handler! List Port Configuration complete LC>18 Nov 2013 21:00:00 Leave LC and return to main menu (Y,N)? y List Configuration sub menu complete > |  |
| --- | --- |

# Bug 139

| Summary: | QCA > Port > able to add, save and upload a IEC61850 port without defining all of the required configuration. |  |  |
| --- | --- | --- | --- |
| Product: | QNet_R2 | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | Java (QCA) | Assignee: | Grant Irani <girani@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | dplatten@qualitrolcorp.com, girani@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | 2.2.3 |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-11-18 16:05:00 EST QCA > Port > able to add, save and upload a IEC61850 port without defining all of the required configuration. i.e. >lc QNet4100 Station number: 1 18 Nov 2013 21:08:21 LC>lp List Port Configuration Port group 1: Port0: console Serial port 0, 38400, 8-N-1, UTC netcon: console, Network port 21000, Local Port group 32: (time-sorted) PortDef2: IEC 61850 Serial port 3, FIXED, 0-N-1 Need to add protocol display handler! List Port Configuration complete |  |
| --- | --- |

# Bug 117

| Summary: | QCA > Time > Time Zone - text should be highlighted green individually for each dropdown as a valid choice is selected. |  |  |
| --- | --- | --- | --- |
| Product: | QNet_R2 | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | Java (QCA) | Assignee: | Grant Irani <girani@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | dplatten@qualitrolcorp.com, girani@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | 2.2.2d |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-11-14 16:52:35 EST QCA > Time > Time Zone - text should be highlighted green individually for each dropdown as a valid choice is selected. currently all 3 boxes are red until all 3 are selected then they all turn green at once. |  |
| --- | --- |

# Bug 118

| Summary: | QCA > Time > Time Zone - if there is only once possible choice in a dropdown it should be automatically selected. |  |  |
| --- | --- | --- | --- |
| Product: | QNet_R2 | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | Java (QCA) | Assignee: | Grant Irani <girani@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | dplatten@qualitrolcorp.com, girani@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | 2.2.2d |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-11-14 16:54:18 EST QCA > Time > Time Zone - if there is only once possible choice in a dropdown it should be automatically selected. also if it is automatically selected it should be highlighted in green text. |  |
| --- | --- |

# Bug 120

| Summary: | QCA>Network>DNS table,Host table,Routing table - cannot add a row if no rows exist in the table. |  |  |
| --- | --- | --- | --- |
| Product: | QNet_R2 | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | Java (QCA) | Assignee: | Grant Irani <girani@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | dplatten@qualitrolcorp.com, girani@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | 2.2.3 |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |
| Attachments: | pic 1 |  |  |

| Description David Platten 2013-11-15 11:16:36 EST QCA>Network>DNS table,Host table,Routing table - cannot add a row if no rows exist in the table. refer to attached screenshot. steps to reproduce: 1. remove all rows (usually start with only 1) 2. observe no rows exist in a table 3. try to add a new row by right clicking and select "add row" 4. observe that a new row is not created. Comment 1 David Platten 2013-11-15 11:18:48 EST Created attachment 9 [details] pic 1 |  |
| --- | --- |

# Bug 121

| Summary: | QCA>Network>Routing table>Network mask - if the user does not tab off the network mask field before clicking the save button, that field is not saved. |  |  |
| --- | --- | --- | --- |
| Product: | QNet_R2 | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | Java (QCA) | Assignee: | Grant Irani <girani@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | dplatten@qualitrolcorp.com, girani@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | 2.2.3 |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-11-15 11:40:17 EST QCA>Network>Routing table>Network mask - if the user does not tab off the network mask field before clicking the save button, that field is not saved. steps to reproduce: 1. create a new routing table row 2. fill in a 3 fields but don't tab off the network mask field 3. click save 4. load a different config without that new row 5. load the saved config from step 3 6. observe that the network mask was not saved. NOTE: *** this is most likely a general bug that affects any similar field in the app. Please apply the fix to all other similar places that it may occur. |  |
| --- | --- |

# Bug 122

| Summary: | QCA>Network>Routing table> - identical routes may be entered and saved without an error given to the user. |  |  |
| --- | --- | --- | --- |
| Product: | QNet_R2 | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | Java (QCA) | Assignee: | Grant Irani <girani@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | dplatten@qualitrolcorp.com, girani@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | 2.2.3 |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-11-15 11:44:28 EST QCA>Network>Routing table> - identical routes may be entered and saved without an error given to the user. expected: unique routes to be enforced in data validation. |  |
| --- | --- |

# Bug 31

| Summary: | Selecting the BPA protocol on the Port tab freezes the JUI. |  |  |
| --- | --- | --- | --- |
| Product: | QNet_R2 | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | Java (QCA) | Assignee: | Grant Irani <girani@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | major | CC: | dplatten@qualitrolcorp.com, girani@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-10-29 09:46:50 EDT Selecting the BPA protocol on the Port tab freezes the JUI. The application appears to be in an endless loop. In the java console the message that keeps repeating is : "Cannot find Mark in range for level 0 using 0" Note that this happens with the data protocol as well and probably others. DP - Retest with version 2.2.2 and confirm still exisits or fixed. 7/16/2013 - problem still exists. - DP PF - Need Java Resource old id 352 |  |
| --- | --- |

# Bug 106

| Summary: | QCA configuration file names containing a periods "." are not displayed in the xml file open or upload dialogs |  |  |
| --- | --- | --- | --- |
| Product: | QNet_R2 | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | Java (QCA) | Assignee: | Grant Irani <girani@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | dplatten@qualitrolcorp.com, girani@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | 2.2.2d |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-11-12 12:00:56 EST QCA configuration file names containing a periods "." are not displayed in the xml file open or upload dialogs this is the filename: The_QNet4100_in_IP_eng_lab_next_to_CQC_lab._v2.xml |  |
| --- | --- |

# Bug 123

| Summary: | QCA>Port> - the user is able to remove Port0 |  |  |
| --- | --- | --- | --- |
| Product: | QNet_R2 | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | Java (QCA) | Assignee: | Grant Irani <girani@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | dplatten@qualitrolcorp.com, girani@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | 2.2.3 |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-11-15 11:56:51 EST QCA>Port> - the user is able to remove Port0. expected: not to be able to delete Port0. |  |
| --- | --- |

# Bug 107

| Summary: | Source row is incorrect sometimes in the dialog box for "Apply to multiple points" function on the Scanner tab in the QCA |  |  |
| --- | --- | --- | --- |
| Product: | QNet_R2 | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | Java (QCA) | Assignee: | Grant Irani <girani@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | dplatten@qualitrolcorp.com, girani@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | 2.2.2d |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |
| Attachments: | incorrect source row |  |  |

| Description David Platten 2013-11-12 14:13:10 EST Source row is incorrect sometimes in the dialog box for "Apply to multiple points" function on the Scanner tab in the QCA. Right clicked on the point 325 and selected apply to multiple rows. Source row in the dialog box is 3205 instead of 325. Comment 1 David Platten 2013-11-12 14:15:10 EST Created attachment 3 [details] incorrect source row |  |
| --- | --- |

# Bug 110

| Summary: | QCA - Scanner Tab - Using "Apply data to Multiple rows" function resulted with the application in an endless loop |  |  |
| --- | --- | --- | --- |
| Product: | QNet_R2 | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | Java (QCA) | Assignee: | Grant Irani <girani@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | dplatten@qualitrolcorp.com, girani@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | 2.2.2d |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-11-12 15:21:34 EST QCA - Scanner Tab - Using "Apply data to Multiple rows" function resulted with the application in an endless loop. Killed the javaw.exe process after it was running for 30 minutes. steps to reproduce: enabled 6 scanners. points from 1 to 384 opened QCA select scanner tab select scanner 1 select point 64 check critical check enable select Auto for sequence right click point 64 and select "apply data to multiple rows" check critical, enable and sequence put 1-384 in the point range textbox click Ok observe the system does not complete the request. |  |
| --- | --- |

# Bug 111

| Summary: | QCA error message when cannot communicate to QNet is not user friendly. |  |  |
| --- | --- | --- | --- |
| Product: | QNet_R2 | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | Java (QCA) | Assignee: | Grant Irani <girani@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | dplatten@qualitrolcorp.com, girani@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |
| Attachments: | pic 1 |  |  |

| Description David Platten 2013-11-14 11:17:45 EST QCA error message when cannot communicate to QNet is not user friendly. refer to attached pic. Comment 1 David Platten 2013-11-14 11:19:28 EST Created attachment 4 [details] pic 1 |  |
| --- | --- |

# Bug 112

| Summary: | "Uploading configuration to QNet..." info box is not removed if the file cannot be uploaded to the controller. |  |  |
| --- | --- | --- | --- |
| Product: | QNet_R2 | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | Java (QCA) | Assignee: | Grant Irani <girani@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | dplatten@qualitrolcorp.com, girani@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |
| Attachments: | pic 1 |  |  |

| Description David Platten 2013-11-14 11:24:52 EST "Uploading configuration to QNet..." info box is not removed if the file cannot be uploaded to the controller. This results in multiple info boxes stacked on top of one another if the user attempts to upload the file several times. refer to the attached jpeg. Comment 1 David Platten 2013-11-14 11:25:37 EST Created attachment 5 [details] pic 1 |  |
| --- | --- |

# Bug 44

| Summary: | Correct / improve business rules for Java RCT |  |  |
| --- | --- | --- | --- |
| Product: | QNet_R2 | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | Java (QCA) | Assignee: | Grant Irani <girani@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | major | CC: | dplatten@qualitrolcorp.com, girani@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |
| Attachments: | java changes |  |  |

| Description David Platten 2013-10-29 10:13:01 EDT See attachment. change request old id 367 Comment 1 David Platten 2013-10-29 10:14:20 EDT Created attachment 1 [details] java changes added attachment |  |
| --- | --- |

# Bug 113

| Summary: | "Can not access Q4100"....": Unexpected end of file from server" endless loop when trying to upload QCA config file to QNet and cannot communicate. |  |  |
| --- | --- | --- | --- |
| Product: | QNet_R2 | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | Java (QCA) | Assignee: | Grant Irani <girani@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | dplatten@qualitrolcorp.com, girani@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |
| Attachments: | pic 1 |  |  |

| Description David Platten 2013-11-14 11:35:33 EST "Can not access Q4100"....": Unexpected end of file from server" endless loop when trying to upload QCA config file to QNet and cannot communicate. steps to reproduce: 1. attempt to upload config file to controller 2. cannot communicate (for whatever reason) 3. error message pops up (can not access..) 4. java login dialog appears 5. user logs in 6. error message pops up 7. steps 3,4 and 5 repeat in a vicious endless loop until the application is closed quickly in between the steps. refer to attached screenshot. Comment 1 David Platten 2013-11-14 11:38:38 EST Created attachment 6 [details] pic 1 |  |
| --- | --- |

# Bug 114

| Summary: | Next set of authentication dialog boxes appear before the user has submitted the first set of credentials to get to the QCA app. |  |  |
| --- | --- | --- | --- |
| Product: | QNet_R2 | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | Java (QCA) | Assignee: | Grant Irani <girani@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | dplatten@qualitrolcorp.com, girani@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | 2.2.2d |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |
| Attachments: | pic 1 |  |  |

| Description David Platten 2013-11-14 11:47:23 EST Created attachment 7 [details] pic 1 Next set of authentication dialog boxes appear before the user has submitted the first set of credentials to get to the QCA app. This happens if the user does not enter the information right away. After a minute or 2 the next credential dialog box and info message appear. refer to the attached screenshot. |  |
| --- | --- |

# Bug 20

| Summary: | Backup Port is shown incorrect in Modify Ports command |  |  |
| --- | --- | --- | --- |
| Product: | QNet_R2 | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | MCOM | Assignee: | Grant Irani <girani@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | minor | CC: | dplatten@qualitrolcorp.com, pfrench@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-10-29 09:25:38 EDT See attachement If you create a new port and then edit the port before saving the changes, all of the settings are correct except for the backup port which is set to 0 instead of 3. After saving the changes, it is set to 3 correctly. The 3 should be there before saving the changes though, along with all of the other settings that are temporarily saved. DP - Retest in 2.2.2 I cannot reproduce this with current firmware. old id 215 Comment 1 David Platten 2013-10-29 15:49:13 EDT verified not fixed in version 2.2.2d. steps to reproduce: 1. use MC 2. use MP 3. use MP to create a new port 4. portname - enter "console1" 5. enter "Y" 6. enter "console" for protocol 7. enter "2" for serial port 2 8. enter for 8 data bits 9. enter to accept default of "none" parity 10. enter for 9600 baud 11. enter for N hardware flow control 12. enter for N require data set ready 13. enter for N require data carrier detect 14. enter "3" for backup port 3 15. enter to accept UTC time 16. enter to accept port group 1 17. enter the same port name just created above to edit it before saving. enter "console1" 18. observe the settings displayed are correct, but continue. 19. steps through the previously entered values 20. when you get to backup port, observe that it is displaying "0" instead of "3". that is the bug. Comment 2 David Platten 2013-10-29 15:51:23 EDT screen capture when following steps to reproduce: MP>MP Modify Port Configuration Port name? console1 Create a new port (Y,N)? Y Protocol? []? Available protocols: console printer colorprint CRT BPA data annunciator DNP Protocol? []console Setting protocol to: console Network or serial port number (Network or 1,2,3,4,5)? []2 Data bits (7, 8)? [8] Parity (O, E, N)? [N] Baud rate? [9600] Use hardware flow control (Y,N)? [N] Require data set ready (Y,N)? [N] Require data carrier detect (Y,N)? [N] Backup port (1..5)? [2]3 Display Local or UTC time (L,U)? [U] Assign to port group (1..32)? [1] Port name? console1 console1: console Serial port 2, 9600, 8-N-1, UTC Backup port 3 Protocol? [console] Network or serial port number (Network or 1,2,3,4,5)? [2] Data bits (7, 8)? [8] Parity (O, E, N)? [N] Baud rate? [9600] Use hardware flow control (Y,N)? [N] Require data set ready (Y,N)? [N] Require data carrier detect (Y,N)? [N] Backup port (1..5)? [0] Display Local or UTC time (L,U)? [U] Assign to port group (1..32)? [1] Port name? Modify Port Configuration complete MP> |  |
| --- | --- |

# Bug 137

| Summary: | Diagnostic point 19 Network port failure goes into Alarm about 3 minutes after the system is rebooted when 61850 port exists. |  |  |
| --- | --- | --- | --- |
| Product: | QNet_R2 | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | MCOM | Assignee: | Grant Irani <girani@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | dplatten@qualitrolcorp.com, pfrench@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | 2.2.3 |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-11-18 14:45:27 EST Diagnostic point 19 Network port failure goes into Alarm about 3 minutes after the system is rebooted when 61850 port exists. The point returns to normal 1 minute later. It appears to be the 61850 port that is causing the alarm. After deleting that port and rebooting the system, the alarm no longer appears. note: i deleted the network console port first but the alarm still appeared after that. i.e.: Rebooting to load new configuration... €x€x€x€x€x€x€x€x€x€x€x€x€x€x€x€x€x€x€x€x€x QNET 4100 version 2.2.3 release Aug 21 2013 System down 18 Nov 2013 14:31:04 System up 18 Nov 2013 14:31:25 QNet4100 is Primary controller > A 14:31:04.003 #D 1 System Down A 14:31:21.627 #G 1 System Fail Alarm N 14:31:29.986 #D 1 System Up N 14:31:29.986 #G 1 System Fail Normal >rt QNet4100 Station number: 1 18 Nov 2013 14:31:49 Report Time complete >rt QNet4100 Station number: 1 18 Nov 2013 14:33:20 Report Time complete > A 14:34:01.006 #D 19 Network port Failure rt QNet4100 Station number: 1 18 Nov 2013 14:34:08 Report Time complete >N 14:35:01.000 #D 19 Network port Normal >lc QNet4100 Station number: 1 18 Nov 2013 14:35:12 LC>lp List Port Configuration Port group unassigned: newIEC61850: IEC 61850 Edition: 1 Security: None Defined Datasets scan1: s1,s2,s3,s4,s5,s6,s7,s8,s9,s10,s11 GOOSE adapter eth0 GOOSE subscriptions fred: IED peter GID scan1 appID 0001 MAC 01:02:00:0C:07 GCB DS confRev 1 GOOSE output Control Blocks No GOOSE publish blocks are defined Port group 1: Port0: console Serial port 0, 38400, 8-N-1, UTC netcon: console, Network port 21000, Local List Port Configuration complete LC> Leave LC and return to main menu (Y,N)? y List Configuration sub menu complete >mc QNet4100 Station number: 1 18 Nov 2013 14:36:46 Enter password: **** MC>MP Modify Ports sub menu MP>DP Delete Port Configuration Port name? ? netcon newIEC61850 Port name? netcon Delete port (Y,N)? y Port name? Delete Port Configuration complete MP> Leave MP and return to MC menu (Y,N)? y Modify Ports sub menu complete MC> Configuration has been modified. WARNING: System will reboot after changes are saved Save, Restore, or Continue (S,R,C)? s Saving configuration... Rebooting to load new configuration... €x€x€x€x€x€x€x€x€x€x€x€x€x€x€x€x€x€x€x€x€x QNET 4100 version 2.2.3 release Aug 21 2013 System down 18 Nov 2013 14:37:02 System up 18 Nov 2013 14:37:23 QNet4100 is Primary controller >N 14:31:29.986 #D 1 System Up N 14:31:29.986 #G 1 System Fail Normal A 14:34:01.006 #D 19 Network port Failure N 14:35:01.000 #D 19 Network port Normal A 14:37:02.001 #D 1 System Down A 14:37:19.632 #G 1 System Fail Alarm N 14:37:28.626 #D 1 System Up N 14:37:28.626 #G 1 System Fail Normal >rt QNet4100 Station number: 1 18 Nov 2013 14:38:18 Report Time complete > > A 14:40:01.006 #D 19 Network port Failure N 14:41:01.000 #D 19 Network port Normal >mp Improper entry >mc QNet4100 Station number: 1 18 Nov 2013 14:41:10 Enter password: **** MC>MP Modify Ports sub menu MP>DP Delete Port Configuration Port name? ? newIEC61850 Port name? newIEC61850 Delete port (Y,N)? y Port name? Delete Port Configuration complete MP> Leave MP and return to MC menu (Y,N)? y Modify Ports sub menu complete MC> Configuration has been modified. WARNING: System will reboot after changes are saved Save, Restore, or Continue (S,R,C)? s Saving configuration... Rebooting to load new configuration... €x€x€x€x€x€x€x€x€x€x€x€x€x€x€x€x€x€x€x€x€x QNET 4100 version 2.2.3 release Aug 21 2013 System down 18 Nov 2013 14:41:34 System up 18 Nov 2013 14:41:56 QNet4100 is Primary controller >N 14:37:28.626 #D 1 System Up N 14:37:28.626 #G 1 System Fail Normal A 14:40:01.006 #D 19 Network port Failure N 14:41:01.000 #D 19 Network port Normal A 14:41:34.000 #D 1 System Down A 14:41:52.624 #G 1 System Fail Alarm N 14:41:59.560 #D 1 System Up N 14:41:59.560 #G 1 System Fail Normal rt QNet4100 Station number: 1 18 Nov 2013 14:42:52 Report Time complete >rt QNet4100 Station number: 1 18 Nov 2013 14:45:42 Report Time complete >lc QNet4100 Station number: 1 18 Nov 2013 14:46:36 LC>lp List Port Configuration Port group 1: Port0: console Serial port 0, 38400, 8-N-1, UTC List Port Configuration complete LC> Leave LC and return to main menu (Y,N)? y List Configuration sub menu complete >rt QNet4100 Station number: 1 18 Nov 2013 14:46:45 Report Time complete > |  |
| --- | --- |

# Bug 78

| Summary: | user prompted to use fiber for a colorprinter port in the MP command even though fiber is already in use. |  |  |
| --- | --- | --- | --- |
| Product: | QNet_R2 | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | MCOM | Assignee: | Grant Irani <girani@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | dplatten@qualitrolcorp.com, pfrench@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-11-05 10:55:20 EST user prompted to use fiber for a colorprinter port in the MP command even though fiber is already in use. fiber is in use by IRIG-B. found in version 2.2.2d |  |
| --- | --- |

# Bug 79

| Summary: | user prompted to use fiber for an annunciator port in the MP command even though fiber is already in use. |  |  |
| --- | --- | --- | --- |
| Product: | QNet_R2 | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | MCOM | Assignee: | Grant Irani <girani@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | dplatten@qualitrolcorp.com, pfrench@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-11-05 11:02:07 EST user prompted to use fiber for an annunciator port in the MP command even though fiber is already in use. fiber is in use by IRIG-B. found in version 2.2.2d |  |
| --- | --- |

# Bug 80

| Summary: | fiber output in use message given to user when trying to change the same port to use a different port number. |  |  |
| --- | --- | --- | --- |
| Product: | QNet_R2 | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | MCOM | Assignee: | Grant Irani <girani@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | dplatten@qualitrolcorp.com, pfrench@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-11-05 11:08:49 EST fiber output in use message given to user when trying to change the same port to use a different port number. create a port, use port 5, use fiber, go through prompts, go to same portname to edit settings of what you just did, pick port 1 instead, now see the "fiber port used" warning about the port you are trying to change. steps to reproduce: MP>mp Modify Port Configuration Port name? test Create a new port (Y,N)? y Protocol? []printer Setting protocol to: printer Serial port number (1..5)? []5 Use fiber interface (Y,N)?[Y]y Data bits (7, 8)? [8] Parity (O, E, N)? [N] Baud rate? [9600] Use hardware flow control (Y,N)? [N] Require data set ready (Y,N)? [N] Require data carrier detect (Y,N)? [N] Backup port (1..5)? [5] Display Local or UTC time (L,U)? [U] Assign to port group (1..32)? [1] Port name? test test: printer Serial port 5, 9600, 8-N-1, UTC FIBER Protocol? [printer] Serial port number (1..5)? [5]1 Fiber output in use by port 5 |  |
| --- | --- |

# Bug 81

| Summary: | "Fiber output in use by port 5" warning displayed to the user when port 5 is not in use. |  |  |
| --- | --- | --- | --- |
| Product: | QNet_R2 | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | MCOM | Assignee: | Grant Irani <girani@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | dplatten@qualitrolcorp.com, pfrench@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-11-05 11:16:21 EST "Fiber output in use by port 5" warning displayed to the user when port 5 is not in use. found in 2.2.2d steps to reproduce: MP>MP Modify Port Configuration Port name? console1 Create a new port (Y,N)? y Protocol? []console Setting protocol to: console Network or serial port number (Network or 1,2,3,4,5)? []1 Fiber output in use by port 5 Data bits (7, 8)? [8] Parity (O, E, N)? [N] Baud rate? [9600] Use hardware flow control (Y,N)? [N] Require data set ready (Y,N)? [N] Require data carrier detect (Y,N)? [N] Backup port (1..5)? [1] Display Local or UTC time (L,U)? [U] Assign to port group (1..32)? [1] Port name? Modify Port Configuration complete MP>lp List Port Configuration Port group 1: Port0: console Serial port 0, 38400, 8-N-1, UTC console1: console Serial port 1, 9600, 8-N-1, UTC List Port Configuration complete MP> |  |
| --- | --- |

# Bug 144

| Summary: | MP command - stuck in endless prompt loop at the "Dataset []?" prompt when adding a new 61850 port |  |  |
| --- | --- | --- | --- |
| Product: | QNet_R2 | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | MCOM | Assignee: | Grant Irani <girani@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | dplatten@qualitrolcorp.com, pfrench@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | 2.2.3 |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-12-02 15:46:11 EST MP command - stuck in endless prompt loop at the "Dataset []?" prompt when adding a new 61850 port. Steps to reproduce: MC>MP Modify Ports sub menu MP>MP Modify Port Configuration Port name? ? Port0 Port name? IEC61850_23port Create a new port (Y,N)? y Protocol? [none]? Available protocols: none console printer colorprint CRT BPA data annunciator DNP 61850 60870 Modbu s Protocol? [none]61850 Setting protocol to: 61850 Edition (1,2)? [1] Use weak security (Y,N)? [N] DataSet name?scanner1 Create a new DataSet (Y,N)? y Description []?scanner 1 points DataSet members?[]? IEC 61850 DataSet list Construct list of points separated by commas. :List items are Sn, Xn, Dn, or Gn, where n is the point index for that point typ e: Sn for scanner point, Xn for remote point, Dn for diagnostic, or Gn for output p oint Specify attributes by adding S (value), Q (quality), or T (time) after the index If no attribute is specifed, the Data Object will be used as the DataSet member DataSet members?[]s1,s2,s3 DataSet name?scanner2 Create a new DataSet (Y,N)? y Description []?scanner 2 points DataSet members?[]s65,s66,s67 DataSet name? GOOSE adapter (eth0, eth1)? [eth0] GOOSE subscription name? GOOSE control block name? goose23 Create a new GOOSE publish block (Y,N)? y GOOSE ID []?gooseID23 VLAN ID [000]? VLAN PRI.[4]? appID [0000]?1234 MacAddr []?? DataSet []? DataSet []? DataSet []? DataSet []?? DataSet does not exist. Available DataSets: scanner1: s1,s2,s3 scanner2: s65,s66,s67 DataSet []? DataSet []? |  |
| --- | --- |

# Bug 82

| Summary: | backup port for printer port can be assigned to an already used serial port (being used as a console port) |  |  |
| --- | --- | --- | --- |
| Product: | QNet_R2 | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | MCOM | Assignee: | Grant Irani <girani@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | dplatten@qualitrolcorp.com, pfrench@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-11-05 11:28:06 EST backup port for printer port can be assigned to an already used serial port (being used as a console port) found in 2.2.2d steps to reproduce: Port name? test2 test2: console Serial port 1, 9600, 8-N-1, UTC Backup port 5 Protocol? [console]printer Setting protocol to: printer Serial port number (1..5)? [1]5 Serial port already in use by test Serial port number (1..5)? []1 Fiber output in use by port 5 Data bits (7, 8)? [8] Parity (O, E, N)? [N] Baud rate? [9600] Use hardware flow control (Y,N)? [N] Require data set ready (Y,N)? [N] Require data carrier detect (Y,N)? [N] Backup port (1..5)? [1]5 Display Local or UTC time (L,U)? [U] Comment 1 Peter French 2013-11-12 11:03:49 EST This is a leagal setting! 'Backup Port' should allow for printer to console backup and vice versa. |  |
| --- | --- |

# Bug 119

| Summary: | Able to create more than one IEC61850 port |  |  |
| --- | --- | --- | --- |
| Product: | QNet_R2 | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | MCOM | Assignee: | Grant Irani <girani@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | dplatten@qualitrolcorp.com, pfrench@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | 2.2.3 |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-11-15 10:33:55 EST Able to create more than one IEC61850 port. in example: MP>lp List Port Configuration Port group unassigned: test: IEC 61850 Edition: 1 Security: None Defined Datasets scan1: s1,s2,s3,s4,s5,s6,s7,s8,s9,s10,s11 GOOSE adapter eth0 GOOSE subscriptions fred: IED peter GID scan1 appID 0001 MAC 01:02:00:0C:07 GCB DS scan1 conf Rev 1 GOOSE output Control Blocks chloe: duck VLAN ID 000 PRI 4 appID 0002 MAC datSet scan1 test2: IEC 61850 Edition: 1 Security: None Defined Datasets scan1: s1,s2,s3,s4,s5,s6,s7,s8,s9,s10,s11 GOOSE adapter eth0 GOOSE subscriptions fred: IED peter GID scan1 appID 0001 MAC 01:02:00:0C:07 GCB DS scan1 conf Rev 1 GOOSE output Control Blocks chloe: duck VLAN ID 000 PRI 4 appID 0002 MAC datSet scan1 Port group 1: Port0: console Serial port 0, 38400, 8-N-1, UTC List Port Configuration complete MP> |  |
| --- | --- |

# Bug 84

| Summary: | Annunciator configuration port is not cleared after option R to restore configuration on exit of the MC command. |  |  |
| --- | --- | --- | --- |
| Product: | QNet_R2 | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | MCOM | Assignee: | Grant Irani <girani@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | dplatten@qualitrolcorp.com, pfrench@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-11-05 14:28:29 EST Annunciator configuration port is not cleared after option R to restore configuration on exit of the MC command. found in 2.2.2d steps to reproduce: >MC QNet4100 Station number: 1 2 Nov 2012 2:08:28 c Enter password: **** MC>MP Modify Ports sub menu MP>MP Modify Port Configuration Port name? annuciatorPort Create a new port (Y,N)? y Protocol? []? Available protocols: console printer colorprint CRT BPA data annunciator DNP Protocol? []annun Setting protocol to: annunciator Serial port number (1..5)? []4 Baud rate? [38400] Annunciator Configuration port (1..5, or 0 to disable)? [0]5 Assign to port group (1..32)? [1] Port name? Modify Port Configuration complete MP>lp List Port Configuration Annunciator configuration Serial port 5, 9600-N-1 Port group 1: Port0: console Serial port 0, 38400, 8-N-1, UTC annuciatorPort: annunciator Serial port 4, 38400, 8-N-1 List Port Configuration complete MP> Leave MP and return to MC menu (Y,N)? y Modify Ports sub menu complete MC> Configuration has been modified. WARNING: System will reboot after changes are saved Save, Restore, or Continue (S,R,C)? r Restoring configuration... Modify Configuration sub menu complete >lc QNet4100 Station number: 1 2 Nov 2012 2:09:27 c LC>lp List Port Configuration Annunciator configuration Serial port 5, 9600-N-1 Port group 1: Port0: console Serial port 0, 38400, 8-N-1, UTC List Port Configuration complete LC> |  |
| --- | --- |

# Bug 91

| Summary: | LP command - Local time designation is not displayed for DNP port set to local time. |  |  |
| --- | --- | --- | --- |
| Product: | QNet_R2 | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | MCOM | Assignee: | Grant Irani <girani@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | dplatten@qualitrolcorp.com, pfrench@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | 2.2.2d |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-11-07 17:08:59 EST LP command - Local time designation is not displayed for DNP port set to local time. In the example below notice that port0 is marked as having local time and the BPA port indicates UTC time. steps to reproduce: MC>MP Modify Ports sub menu MP>MP Modify Port Configuration Port name? DNP Create a new port (Y,N)? Y Protocol? []? Available protocols: console printer colorprint CRT BPA data annunciator DNP Protocol? []DNP Setting protocol to: DNP Network or serial port number (Network or 1,2,3,4,5)? []4 Baud rate? [9600] Maximum number of events in report (0..100)? [50] Master station address (1..65500)? [65000] Station address (1..65500)? [1] Use localtime as DNP time? [N]Y Assign to port group (1..32)? [1] Port name? Modify Port Configuration complete MP>LP List Port Configuration Port group 1: Port0: console Serial port 0, 38400, 8-N-1 , Local bpaport: BPA Serial port 1, 9600, 8-N-1 , UTC DNP: DNP Serial port 4, 9600, 8-N-1 Master station address 65000 Station address 1 Event group size 50 List Port Configuration complete MP> |  |
| --- | --- |

# Bug 102

| Summary: | 65000 accepted as a DNP server port number when using the MP command to create a DNP port |  |  |
| --- | --- | --- | --- |
| Product: | QNet_R2 | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | MCOM | Assignee: | Grant Irani <girani@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | dplatten@qualitrolcorp.com, pfrench@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-11-11 11:28:54 EST 65000 accepted as a DNP server port number when using the MP command to create a DNP port. NOTE: when editing the port again, the port number is displayed as negative: i.e. "DNP server port number (0-65535)? [-536]" steps to reproduce: MC>MP Modify Ports sub menu MP>LP List Port Configuration Port group 1: Port0: console Serial port 0, 38400, 8-N-1, Local List Port Configuration complete MP>MP Modify Port Configuration Port name? DNPnetUDP Create a new port (Y,N)? y Protocol? []? Available protocols: console printer colorprint CRT BPA data annunciator DNP Protocol? []DNP Setting protocol to: DNP Network or serial port number (Network or 1,2,3,4,5)? []net UDP or TCP? [TCP]u DNP server port number (0-65535)? [20000]65000 Master station IP address (*.*.*.* allows any)? [*.*.*.*]65000 Comment 1 Peter French 2013-11-12 11:10:13 EST Suggest also changing 'DNP server port number (0-65535)?' to 'Network port number (0..65535)?' to be consistant with other protocols. |  |
| --- | --- |

# Bug 124

| Summary: | No escape from MX command, "GOOSE DO: index? " prompt. |  |  |
| --- | --- | --- | --- |
| Product: | QNet_R2 | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | MCOM | Assignee: | Grant Irani <girani@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | dplatten@qualitrolcorp.com, pfrench@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | 2.2.3 |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-11-18 11:45:09 EST No escape from MX command, "GOOSE DO: index? " prompt. steps to reproduce: 1. no subscriptions configured. 2. carriage return entered for the "GOOSE subscription name? " prompt. 3. observe that numbers, letters or words are not accepted. tried CR, decimal point, question mark, cannot get out of the command without rebooting the device. |  |
| --- | --- |

# Bug 35

| Summary: | Security download file access problem |  |  |
| --- | --- | --- | --- |
| Product: | QNet_R2 | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | MCOM | Assignee: | Grant Irani <girani@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | major | CC: | dplatten@qualitrolcorp.com, pfrench@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-10-29 09:57:04 EDT After an 'SD Download Security files' command, subsequent use of the SD command causes a following error message: WARNING: can't open config file: /home/openssl/openssl.cnf WARNING: can't open cf Error is persistant until system is rebooted. DP - Confirm fixed in next version. Re- test in User mode not factory. Not an error, (message should be blocked in user mode). Can be corrected by supplying a director /home/openssl with an empty openssl.conf file. old id 357 Comment 1 David Platten 2013-11-05 15:14:19 EST verified still exists in 2.2.2d and in user mode. steps to reproduce: >UL QNet4100 Station number: 1 2 Nov 2012 2:46:45 c User Login Enter user name: security Enter password: ******** User Login complete >? ? Context Help UO User Logout CP Change Password SU Upload Security Files to QNet SD Download Security Files from QNet AR Adjust User Roles LU List Users AU Add New User DU Delete User >SD QNet4100 Station number: 1 2 Nov 2012 2:47:15 c Start XMODEM receiver Download Security Files from QNet complete >SD QNet4100 Station number: 1 2 Nov 2012 2:47:47 c WARNING: can't open config file: /home/openssl/openssl.cnf WARNING: can't open co nfig file: /home/openssl/openssl.cnf Start XMODEM receiver Download Security Files from QNet complete > A 02:48:01.000 #D 13 Port 0 Failure A 02:48:01.003 #G 2 System Fault Alarm N 02:49:01.000 #D 13 Port 0 Normal N 02:49:01.008 #G 2 System Fault Normal >MC User is not authorized to use command >? ? Context Help UO User Logout CP Change Password SU Upload Security Files to QNet SD Download Security Files from QNet AR Adjust User Roles LU List Users AU Add New User DU Delete User >UO User Logout complete >MC QNet4100 Station number: 1 2 Nov 2012 2:49:33 c Enter password: **** MC>XQ Reset QNet System Rebooting after reset command... €x€x€x€x€x€x€x€x€x€x€x€x€x€x€x€x€x€x€x€x€x QNET 4100 version 2.2.2d release Jul 16 2013 System down 2 Nov 2012 2:49:37 System up 2 Nov 2012 2:49:59 QNet4100 is Primary controller > A 02:49:37.000 #D 1 System Down A 02:49:55.660 #G 1 System Fail Alarm N 02:50:03.340 #D 1 System Up N 02:50:03.340 #G 1 System Fail Normal |  |
| --- | --- |

# Bug 125

| Summary: | A carriage return is accepted as valid input at the "GOOSE subscription name? " prompt in the MX command. |  |  |
| --- | --- | --- | --- |
| Product: | QNet_R2 | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | MCOM | Assignee: | Grant Irani <girani@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | dplatten@qualitrolcorp.com, pfrench@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | 2.2.3 |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-11-18 11:58:07 EST A carriage return is accepted as valid input at the "GOOSE subscription name? " prompt in the MX command. Other text entries are rejected as an invalid subscription name but a carriage return is allowed. expected: only valid subscription names are allowed at this prompt. suggestion: dont allow use of the MX command if there is not a 61850 port configured. steps to reproduce: 1. no 61850 port configured 2. therefore no subscriptions exist 3. use the MX command 4. enter CR at the above prompt 5. observe it is accepted Comment 1 David Platten 2013-11-18 11:59:31 EST example: MC>MX Modify External Definitions Multipoint, Range, Single (M,R,S)? S Point (1..1024)? 1 1 Point is not configured Remote point type? [none]61850 GOOSE subscription name? COOKED Not a valid GOOSE subscription GOOSE subscription name? GOOD Not a valid GOOSE subscription GOOSE subscription name? GOOSE Not a valid GOOSE subscription GOOSE subscription name? GOOSE DO:index? |  |
| --- | --- |

# Bug 40

| Summary: | NTP not working |  |  |
| --- | --- | --- | --- |
| Product: | QNet_R2 | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | MCOM | Assignee: | Grant Irani <girani@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | major | CC: | dplatten@qualitrolcorp.com, pfrench@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-10-29 10:06:27 EDT SER time is not updated to NTP time when Precision time source is lost. Need to develop specification for NTP time synchronization of SER clock when precission time source is lost. PF - Is this acceptable? System has two time sources - linux time (adjusted by NTP) and SERtime (adjusted by precision time source). If precision time source is working, the linux system time will be set from SERtime when the deviation exceeds 10ms If precision time is unvailable, SERtime is set from linux time if deviation exceeds 100ms. old id 362 Comment 1 David Platten 2013-11-07 10:38:33 EST verified not fixed in 2.2.2d. Comment 2 David Platten 2013-11-07 11:25:00 EST now it is 30 minutes after i declared that the bug was not fixed but the time appears to be synchronizing to the NTP server. I assumed the synchronization would be very fast but maybe it takes several minutes and several updates? after 5 to 10 minutes it looked like it had synched to the ntp server but it was 3 seconds off. But now it is right on. This synchronization and update needs to occur faster. Comment 3 David Platten 2013-11-07 13:51:26 EST update: tried this again but this time it did not synchronize. so either it synchronized last time and not this time or it didn't really synchronize last time. Comment 4 David Platten 2013-11-07 13:52:58 EST update to my last comment... it has been 2 hours and 21 minutes since the precision time source was lost. |  |
| --- | --- |

# Bug 133

| Summary: | Deleting DataSet of a 61850 port does not delete the DataSet. |  |  |
| --- | --- | --- | --- |
| Product: | QNet_R2 | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | MCOM | Assignee: | Grant Irani <girani@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | dplatten@qualitrolcorp.com, pfrench@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | 2.2.3 |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-11-18 13:58:49 EST Deleting DataSet of a 61850 port does not delete the DataSet. in example: MP>MP Modify Port Configuration Port name? ? Port0 netcon IEC61850dave Port name? IEC61850dave IEC61850dave: IEC 61850 Edition: 1 Security: None Defined Datasets scan1: s1,s2,s3,s4,s5,s6,s7,s8,s9,s10,s11 GOOSE adapter eth0 GOOSE subscriptions fred: IED peter GID scan1 appID 0001 MAC 01:02:00:0C:07 GCB DS confRev 1 GOOSE output Control Blocks No GOOSE publish blocks are defined Protocol? [61850] Edition (1,2)? [1] Use weak security (Y,N)? [N] DataSet name?? scan1: s1,s2,s3,s4,s5,s6,s7,s8,s9,s10,s11 DataSet name?scan1 DataSet: Delete this DataSet (Y,N)? Y DataSet name?? scan1: s1,s2,s3,s4,s5,s6,s7,s8,s9,s10,s11 DataSet name? |  |
| --- | --- |

# Bug 42

| Summary: | Add fixed time zones |  |  |
| --- | --- | --- | --- |
| Product: | QNet_R2 | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | MCOM | Assignee: | Grant Irani <girani@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | major | CC: | dplatten@qualitrolcorp.com, girani@qualitrolcorp.com, pfrench@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-10-29 10:09:40 EDT [VOC - ATCO: operates in fixed mountain standard time (MST) and needs to be able to set UTC offset to a fixed number so that all com ports / protocols report events in MST, even when local time switches to daylight saving.] Other utilities are likely to have the same issue. dd/zoneinfo/Etc/ provides fixed time zones for: GMT0 (=UTC) GMT+0, GMT+1, GMT+2, … up to GMT+12 GMT-0, GMT-1,GMT-2,.. Up to GMT-14 Greenwich (=GMT =UTC) UTC (=UTC) UCT (=UTC) Universal (=UTC) Zulu (=UTC) Currently 'maketzdirs.sh' uses 'zone.tab' and 'ISO3166.tab' tables to create links to zone files. These tables do not include these fixed zones. MZ command allows the time zone to set by asking for region, country and timezone. MZ uses the linked directory structure to create a list of available reqions, countries and timezones. Modifying maketzdirs.sh to add links for the GMT zones with a region of FixedOffset and contry of FixedOffset to link to GMT, GMT+ and GMT- zoneinfo files. PF - Retest in next release Update maketimezones to add directories and links as described. change request old id 364 Comment 1 David Platten 2013-11-07 14:25:15 EST did not see a choice for "FixedOffset" in the Region prompt for the MZ command. verified not fixed in 2.2.2d. Comment 2 Peter French 2013-11-12 10:49:03 EST This does appear to be fixed in 2.2.3 dev tree... Needs to migrate to 2.2.2 patch Comment 3 Grant Irani 2013-12-06 12:59:42 EST The FixedOffset directory structure was not included in the patch (usually the timezone info is in the timezone tgz of a new install, and wasn't on the build directory structure). The qnettimezones have been tarred (to preserve the links) and made available in the new patch kit. |  |
| --- | --- |

# Bug 134

| Summary: | Deleting subscription name of a 61850 port does not delete the subscription name. |  |  |
| --- | --- | --- | --- |
| Product: | QNet_R2 | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | MCOM | Assignee: | Grant Irani <girani@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | dplatten@qualitrolcorp.com, pfrench@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | 2.2.3 |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-11-18 14:02:08 EST Deleting subscription name of a 61850 port does not delete the subscription name. in example: MP>MP Modify Port Configuration Port name? ? Port0 netcon IEC61850dave Port name? IEC61850dave IEC61850dave: IEC 61850 Edition: 1 Security: None Defined Datasets scan1: s1,s2,s3,s4,s5,s6,s7,s8,s9,s10,s11 GOOSE adapter eth0 GOOSE subscriptions fred: IED peter GID scan1 appID 0001 MAC 01:02:00:0C:07 GCB DS confRev 1 GOOSE output Control Blocks No GOOSE publish blocks are defined Protocol? [61850] Edition (1,2)? [1] Use weak security (Y,N)? [N] DataSet name? GOOSE adapter (eth0, eth1)? [eth0] GOOSE subscription name? ? fred: IED peter GID scan1 appID 0001 MAC 01:02:00:0C:07 GCB DS confRev 1 GOOSE subscription name? fred fred: IED peter GID scan1 appID 0001 MAC 01:02:00:0C:07 GCB DS confRev 1 Delete this GOOSE subscription (Y,N)? Y GOOSE subscription name? ? fred: IED peter GID scan1 appID 0001 MAC 01:02:00:0C:07 GCB DS confRev 1 GOOSE subscription name? |  |
| --- | --- |

# Bug 18

| Summary: | Port is still created after the "All serial ports are already in use" error message |  |  |
| --- | --- | --- | --- |
| Product: | QNet_R2 | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | MCOM | Assignee: | Grant Irani <girani@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | minor | CC: | dplatten@qualitrolcorp.com, pfrench@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-10-29 09:21:15 EDT maybe fix in next release. Need a bail out mechnism from MP when user enters a serial port and "All serial ports already in use". DP - Need test in next version Modified to delete new port if serial only protocol is selected for new port and all ports are in use. 2.2e Comment 1 David Platten 2013-10-29 09:21:37 EDT old id 84 Comment 2 David Platten 2013-10-29 14:46:51 EDT will check in version 2.2.2e Comment 3 David Platten 2013-11-06 11:11:17 EST verified not fixed in 2.2.2d. Grant, is there a 2.2.2e? |  |
| --- | --- |

# Bug 135

| Summary: | The configuration for a 61850 port is not deleted when the port is deleted. |  |  |
| --- | --- | --- | --- |
| Product: | QNet_R2 | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | MCOM | Assignee: | Grant Irani <girani@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | dplatten@qualitrolcorp.com, pfrench@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | 2.2.3 |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-11-18 14:17:46 EST The configuration for a 61850 port is not deleted when the port is deleted. note in the example below, that the dataset name and subscription name already exist and are not added when the port is created, but they are left over from the previous port that was deleted. i.e.: >MC QNet4100 Station number: 1 18 Nov 2013 14:12:11 Enter password: **** MC>MP Modify Ports sub menu MP>DP Delete Port Configuration Port name? ? netcon IEC61850dave Port name? IEC61850dave Delete port (Y,N)? y Port name? Delete Port Configuration complete MP>lp List Port Configuration Port group 1: Port0: console Serial port 0, 38400, 8-N-1, UTC netcon: console, Network port 21000, Local List Port Configuration complete MP> Leave MP and return to MC menu (Y,N)? y Modify Ports sub menu complete MC> Configuration has been modified. WARNING: System will reboot after changes are saved Save, Restore, or Continue (S,R,C)? s Saving configuration... Rebooting to load new configuration... €x€x€x€x€x€x€x€x€x€x€x€x€x€x€x€x€x€x€x€x€x QNET 4100 version 2.2.3 release Aug 21 2013 System down 18 Nov 2013 14:12:58 System up 18 Nov 2013 14:13:19 QNet4100 is Primary controller >N 12:27:43.679 #D 1 System Up N 12:27:43.679 #G 1 System Fail Normal A 12:30:01.005 #D 19 Network port Failure N 12:31:01.003 #D 19 Network port Normal 18 Nov 2013 13:00:00 18 Nov 2013 14:00:00 A 14:12:58.003 #D 1 System Down A 14:13:15.627 #G 1 System Fail Alarm N 14:13:24.262 #D 1 System Up N 14:13:24.262 #G 1 System Fail Normal rt QNet4100 Station number: 1 18 Nov 2013 14:17:25 Report Time complete >rt QNet4100 Station number: 1 18 Nov 2013 14:18:42 Report Time complete >MC QNet4100 Station number: 1 18 Nov 2013 14:19:13 Enter password: **** MC>MP Modify Ports sub menu MP>MP Modify Port Configuration Port name? ? Port0 netcon Port name? newIEC61850 Create a new port (Y,N)? y Protocol? [none]61850 Setting protocol to: 61850 Edition (1,2)? [1] Use weak security (Y,N)? [N] DataSet name?? scan1: s1,s2,s3,s4,s5,s6,s7,s8,s9,s10,s11 DataSet name? GOOSE adapter (eth0, eth1)? [eth0] GOOSE subscription name? ? fred: IED peter GID scan1 appID 0001 MAC 01:02:00:0C:07 GCB DS confRev 1 GOOSE subscription name? GOOSE control block name? Port name? Modify Port Configuration complete MP>lp List Port Configuration Port group unassigned: newIEC61850: IEC 61850 Edition: 1 Security: None Defined Datasets scan1: s1,s2,s3,s4,s5,s6,s7,s8,s9,s10,s11 GOOSE adapter eth0 GOOSE subscriptions fred: IED peter GID scan1 appID 0001 MAC 01:02:00:0C:07 GCB DS confRev 1 GOOSE output Control Blocks No GOOSE publish blocks are defined Port group 1: Port0: console Serial port 0, 38400, 8-N-1, UTC netcon: console, Network port 21000, Local List Port Configuration complete MP> |  |
| --- | --- |

# Bug 75

| Summary: | "PPS on fiber?" prompt not displayed after selecting IRIG-B for time source |  |  |
| --- | --- | --- | --- |
| Product: | QNet_R2 | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | MCOM | Assignee: | Grant Irani <girani@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | dplatten@qualitrolcorp.com, pfrench@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-11-05 10:32:02 EST "PPS on fiber?" prompt not displayed after selecting IRIG-B for time source PPS is available on the fiber only when the fiber is connected to the PIC, therefore only when the user selects IRIG-B, NMEA with a PPS on FIBER option, or PPS in for time synch source. When fiber is used for the serial ports PPS is not available on the fiber. suggestion: to remove the "PPS on fiber?" altogether, and the equivalent in the JUI. If we do this should we also remove the "PPS on fiber" line in the configuration summary? (LC, LQ). Comment 1 David Platten 2013-11-05 10:33:22 EST start of suggestion should be: to remove the "PPS on fiber?" prompt altogether... Comment 2 Peter French 2013-11-12 10:56:59 EST Suggest we should leave the 'PPS on fiber' in the LC/LQ: By default (if fiber is not assigned as a serial port or is not assigned for time sync) PPS on fiber = Y. If Fiber is assigned for time sync then PPS on Fiber = Y. If fiber is assigned to serial then PPS on Fiber = N. We do not need to ask the question since it will always be Y unless we are using Fiber fr serial! |  |
| --- | --- |

# Bug 76

| Summary: | user prompted to use fiber for printer port in the MP command even though fiber is already in use. |  |  |
| --- | --- | --- | --- |
| Product: | QNet_R2 | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | MCOM | Assignee: | Grant Irani <girani@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | dplatten@qualitrolcorp.com, pfrench@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-11-05 10:47:41 EST user prompted to use fiber for printer port in the MP command even though fiber is already in use. fiber is in use by IRIG-B. Comment 1 David Platten 2013-11-05 10:49:11 EST found in version 2.2.2d |  |
| --- | --- |

# Bug 30

| Summary: | Ethernet fiber optic not working |  |  |
| --- | --- | --- | --- |
| Product: | QNet_R2 | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | UBoot | Assignee: | Grant Irani <girani@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | major | CC: | dplatten@qualitrolcorp.com, girani@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-10-29 09:44:20 EDT Comment 1 David Platten 2013-10-29 09:45:05 EDT SER does not currently provide setting for "Use Fiber Optic" for Ethernet connections. PF - Grant needs hardware for development: - Controller FO Module - Ethernet to FO converter - FO Cable GI - See attached email from Mark with Uboot code snips… 1. Update Linux to allow PHY to switch from copper to fiber / fiber to copper. 3. Update Config DB and XML to add Etehrnet connection type. 2. Update MCOM to to ask "Use fiber connection (Y,N)? [N]". 3. Update Java to add checkbox for "Use fiber connection". old id 346 Comment 2 David Platten 2013-12-05 09:18:52 EST Grant has hardware now. |  |
| --- | --- |

# Bug 136

| Summary: | Sometimes the Web UI does not restore communication to the box after a reboot. |  |  |
| --- | --- | --- | --- |
| Product: | QNet_R2 | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | Web UI | Assignee: | Grant Irani <girani@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | dplatten@qualitrolcorp.com, pfrench@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | 2.2.3 |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |
| Attachments: | pic 1 |  |  |

| Description David Platten 2013-11-18 14:20:56 EST Sometimes the Web UI does not restore communication to the box after a reboot. see attached screenshot. Comment 1 David Platten 2013-11-18 14:21:52 EST Created attachment 10 [details] pic 1 Comment 2 David Platten 2013-11-18 14:25:28 EST also note the yellow error indicator at the bottom left of the web ui in the browser. |  |
| --- | --- |

# Bug 22

| Summary: | Hyperterm declares Group Alarm Condition when RINGBACK relay is actually in Normal Condition. |  |  |
| --- | --- | --- | --- |
| Product: | QNet_R2 | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | MCOM | Assignee: | Peter French <pfrench@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | minor | CC: | dplatten@qualitrolcorp.com, pfrench@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-10-29 09:29:44 EDT Groups 184 and 194 are configured to operate relays R6 and R8, and relays are configured for 'Ringback' operation. (See 'Bug 248A.txt' attachement). Even though no ringback condition exists (See 'Bug 248.bmp' Adviser screen shot attachment; no points are in the 'resetable steady green condition') and the relays are in the Normal de-energized condition, the RA Summary report shows the group points as in the alarm condition. (See 'Bug 248A.txt' attachement). Group point should be inverted such that the Group is in the 'Alarm' condition only when a ringback condition exists and is in the 'Normal' condition when no ringback condition exists. Note, however, the relay operation is correct; the relay should energize when a ringback condition exists and de-energize when no ringback condition exists (or silence is applied). PF - Need definition old id 248 Comment 1 David Platten 2013-10-29 15:55:12 EDT assigned to Peter. |  |
| --- | --- |

# Bug 23

| Summary: | If date is changed across Daylight savings time the time jumps. |  |  |
| --- | --- | --- | --- |
| Product: | QNet_R2 | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | MCOM | Assignee: | Peter French <pfrench@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | minor | CC: | dplatten@qualitrolcorp.com, pfrench@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-10-29 09:31:35 EDT Note for manual: If Edit time is used at Local Time port and date is changed accros a Daylight savings time boundary, the time will also change since the new date will recalculate time based on time zone settings after the command is complete! Need note in manual. PF - Document as a known issue doc only old id 259 Comment 1 David Platten 2013-10-29 15:56:56 EDT assigned to Peter. |  |
| --- | --- |

# Bug 24

| Summary: | Flow control and hand shaking signal not responding correctly |  |  |
| --- | --- | --- | --- |
| Product: | QNet_R2 | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | MCOM | Assignee: | Peter French <pfrench@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | major | CC: | dplatten@qualitrolcorp.com, pfrench@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-10-29 09:33:28 EDT For MCOM: Port 1: CTS, DSR and DCD must be asserted port before it will receive data, even if these are set to 'N' in configuration. (Port will still transmit data). Port 2: Port will not transmit events if set for DCD = 'Y', unless CTS, DSR and DCD are asserted. Port will not transmit events if set for DSR = 'Y', unless CTS, DSR and DCD are asserted. DP - Need to retest and document results. (No firmware change - We tested this and came to conclusion that Port 1 works slighty different to other ports. Need Clarification for this for documentation only.) PF - Update instruction manual to clarify functionality. doc only old id 288 Comment 1 David Platten 2013-10-29 16:11:35 EDT assigned to Peter. |  |
| --- | --- |

# Bug 25

| Summary: | Port Failure on DN Download Configuration |  |  |
| --- | --- | --- | --- |
| Product: | QNet_R2 | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | MCOM | Assignee: | Peter French <pfrench@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | minor | CC: | dplatten@qualitrolcorp.com, pfrench@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-10-29 09:35:18 EDT Port 0 failure during DN command. Port 0 failed and returned on line approx 2 mins later. Port still responds correctly. Used MC > DN command at Port 0 and initiated several inputs during download. All ports responded correctly during the download. Repeated test at Console Port 1 (Serial Port 1) and confirmed that port failed at start of download, but did not affect event reporting at other ports. Port recovered within 90 seconds after download completed. Repeated test on Console 2 (Network Port) and confirmed system reported ‘network port failure’, but did not affect performance of other ports. Port recovered within 90 seconds after download completed. Conclusion. Bug has no detrimental effect on performance of system and port automatically recovers after download is complete. Bug has no detrimental effect on performance of system and port automatically recovers after download is complete. PF - Document as a known issue doc only old id 296 Comment 1 David Platten 2013-10-29 16:12:50 EDT assigned to Peter. |  |
| --- | --- |

# Bug 85

| Summary: | known issue: Fiber on port 1 does not work properly |  |  |
| --- | --- | --- | --- |
| Product: | QNet_R2 | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | MCOM | Assignee: | Peter French <pfrench@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | dplatten@qualitrolcorp.com, pfrench@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-11-05 16:50:33 EST known issue: Fiber on port 1 does not work properly There is a known handshaking issue regarding fiber on port 1. Configuring as expected will not work. Additional handshaking signals are required. work-around: configure fiber on port 1 as expected, ie. 38400 N,8,1 no flow control connect a serial cable to the serial port 1 connector and open a hypterminal session to it. This will provide the necessary handshaking signals to get the fiber port 1 to work. Peter to document this known issue. seen in 2.2.2d Comment 1 David Platten 2013-11-05 16:51:10 EST note: fiber on port 5 works fine. |  |
| --- | --- |

# Bug 19

| Summary: | Missing feature - ability to set the "time sorted (Y/N)" property of each port |  |  |
| --- | --- | --- | --- |
| Product: | QNet_R2 | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | MCOM | Assignee: | Peter French <pfrench@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | minor | CC: | dplatten@qualitrolcorp.com, pfrench@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-10-29 09:23:20 EDT Setting is on Port page, but affects all ports sharing the group PF - Document only. Need to tell user to use different port groups for sorted / unsorted types. doc only old id 123 |  |
| --- | --- |

# Bug 27

| Summary: | Add patching information to the manual |  |  |
| --- | --- | --- | --- |
| Product: | QNet_R2 | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | Web UI | Assignee: | Peter French <pfrench@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | minor | CC: | dplatten@qualitrolcorp.com, pfrench@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-10-29 09:39:23 EDT PF- Add patching information to the manual doc only old id 316 Comment 1 David Platten 2013-10-31 08:58:34 EDT assigned to Peter. |  |
| --- | --- |

# Bug 56

| Summary: | Rev 3 BUG - input current scaling |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | Albert Burgin <aburgin@qualitrolcorp.com> |
| Component: | TX28 App | Assignee: | Brian Seiffer <bseiffer@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | major | CC: | cbakhos@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | IE8 |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description Albert Burgin 2013-11-01 10:42:45 EDT Current sensors were 50 amps = .333 volts out and 400 amps = .333 volts dc out Analog scaling currently reads about 10000 with a CT ratio of CT Ratio 6006 : 5 1201.2 : 1 |  |
| --- | --- |

# Bug 72

| Summary: | REV 11/4/13 PM - SF6 BAR readings measurement is off |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | Albert Burgin <aburgin@qualitrolcorp.com> |
| Component: | TX28 App | Assignee: | Brian Seiffer <bseiffer@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | blocker | CC: | cbakhos@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | V1.02.00 (11/4/13 pm) |  |  |
| Hardware: | RevA |  |  |
| OS: | IE8 |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description Albert Burgin 2013-11-05 09:22:46 EST Menu: Events and Records > Real Time Monitor The SF6 measurement RTU-1 is wrong. The input pressure is 20-25 PSI. The output should read 1.38 to 1.72 BARs. The SF6 sensor has been Sensor data inputted into the SF6 configuration menu P: low=1, max = 16 T: low = -40, max = 80 D: low = 0, max = 60 |  |
| --- | --- |

# Bug 103

| Summary: | REV 11/8/13 - CT ratio is missing 2nd transformation entry spot & calculation |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | Albert Burgin <aburgin@qualitrolcorp.com> |
| Component: | TX28 App | Assignee: | Brian Seiffer <bseiffer@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | major | CC: | cbakhos@qualitrolcorp.com, girani@qualitrolcorp.com, kmanne@qualitrolcorp.com |
| Priority: | High |  |  |
| Version: | November 8, 2013 PM |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description Albert Burgin 2013-11-11 15:27:09 EST The transformation for San Diego was hard coded into the firmware where .333 volts ac rms yields an output current reading of 96000 amps. This is an actual current transformation of 288288:1. part A) and entry spot is missing under Configure Analog Inputs > AC Currents and Voltages under CT ratio. There needs to be two entries under CT ratio. A multiplier is missing to reflect the "other" current transformation. In San Diego, the 96000 amps displayed in the Current display (A, B & C) comes from two current transformations. 240 : 1 ratio should yield an out put for .333 volts as 80 amps. The real current 96000 amps comes from a second current transformer with a ratio of 96000amps/80 amps or a ratio of 1200:1. This current transformation will vary by site and has no current entry box in the HTML interface. Action Item #1) - A entry box needs to be added to the HTML interface Action Item #2) - This should be used to along with the other current to voltage transformer to provide the correct current transformation. |  |
| --- | --- |

# Bug 57

| Summary: | Rev 3 BUG - Battery voltage is still not reccognized |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | Albert Burgin <aburgin@qualitrolcorp.com> |
| Component: | TX28 App | Assignee: | Brian Seiffer <bseiffer@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | major | CC: | cbakhos@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | IE8 |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description Albert Burgin 2013-11-01 11:08:16 EDT Analog battery voltage still reads 0 volts Verified battery signal is 10 VDC |  |
| --- | --- |

# Bug 73

| Summary: | REV 11/4/13 PM - 0 current has high residual current |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | Albert Burgin <aburgin@qualitrolcorp.com> |
| Component: | TX28 App | Assignee: | Brian Seiffer <bseiffer@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | critical | CC: | cbakhos@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | V1.02.00 (11/4/13 pm) |  |  |
| Hardware: | RevA |  |  |
| OS: | IE8 |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description Albert Burgin 2013-11-05 09:30:45 EST Menu: Events and Records> Real Time Monitor When all current is turned off to the BCM, even with the inputs shorted, the currents read 16 amps AC rms. With just the Labview system off, the noise registers as 130 amps There needs to be a way to zero this offset out |  |
| --- | --- |

# Bug 77

| Summary: | REV 11/4/13 PM - SF6 real time data -Dew point missing |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | Albert Burgin <aburgin@qualitrolcorp.com> |
| Component: | TX28 App | Assignee: | Brian Seiffer <bseiffer@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | blocker | CC: | cbakhos@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | V1.02.00 (11/4/13 pm) |  |  |
| Hardware: | RevA |  |  |
| OS: | IE8 |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description Albert Burgin 2013-11-05 10:55:00 EST Under events and records> real time monitor there is no listing under SF6 for a dew point measurement REQUIRED BY San Diego |  |
| --- | --- |

# Bug 58

| Summary: | REV 11/2/13 - system lock when changing CT ratio |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | Albert Burgin <aburgin@qualitrolcorp.com> |
| Component: | TX28 App | Assignee: | Brian Seiffer <bseiffer@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | blocker | CC: | cbakhos@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | IE8 |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description Albert Burgin 2013-11-02 11:57:06 EDT When changing the CT ratio to 3000:5 indicated as a setting that San Diego may set, BCM real time monitor settings are all 0 |  |
| --- | --- |

# Bug 86

| Summary: | REV 11/5/13 pm-analysis will not start at boot |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | Albert Burgin <aburgin@qualitrolcorp.com> |
| Component: | TX28 App | Assignee: | Brian Seiffer <bseiffer@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | critical | CC: | cbakhos@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | November 5, 2013, 9pm |  |  |
| Hardware: | RevA |  |  |
| OS: | IE8 |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description Albert Burgin 2013-11-06 11:56:15 EST REV 11/5/13 pm-analysis will not start at boot It was noted that with the SF6 sensor connected at BCM boot up, there were no values measured in "Input Checks" or "Real Time" monitor. the system was rebooted several times and will not properly start until the SF6 connector is unplugged. After a proper boot up the SF6 connector can be re-connected. Note: even on good boots, the BCM may have to be rebooted several times until data is properly measured. While seemingly random, the SF6 sensor had a definite impact on how well the BCM rebooted and how many times it took to properly boot This was performed 10-20 times with and with out the SF6 connector connected |  |
| --- | --- |

# Bug 105

| Summary: | REV 11/8/13 - Comtrade Files |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | Albert Burgin <aburgin@qualitrolcorp.com> |
| Component: | TX28 App | Assignee: | Brian Seiffer <bseiffer@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | major | CC: | cbakhos@qualitrolcorp.com, llehmann@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | November 8, 2013 PM |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description Albert Burgin 2013-11-12 08:13:45 EST REV 11/8/13 - Comtrade Files The BCM hardware and software currently doesn't have the ability to create and display captured waveforms. The desired format is in the Comtrade file format. |  |
| --- | --- |

# Bug 59

| Summary: | REV 11/2/13 - Currents not scaling correctly |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | Albert Burgin <aburgin@qualitrolcorp.com> |
| Component: | TX28 App | Assignee: | Brian Seiffer <bseiffer@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | blocker | CC: | cbakhos@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description Albert Burgin 2013-11-04 10:01:09 EST "Screen: Real Time Monitor Screen: input check Analog Inputs ADC-1 Phase current A reads 10500 amps with 0.333 volts peak AC RMS ADC-2 Phase current B reads 10500 amps with 0.333 volts peak AC RMS ADC-3 Phase current C reads 10500 amps with 0.333 volts peak AC RMS Currents should all read 400 amps for a 1200:1 current transformer ratio |  |
| --- | --- |

# Bug 87

| Summary: | REV 11/5/13 pm-random lockups of data in "real time" monitor |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | Albert Burgin <aburgin@qualitrolcorp.com> |
| Component: | TX28 App | Assignee: | Brian Seiffer <bseiffer@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | critical | CC: | cbakhos@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | November 5, 2013, 9pm |  |  |
| Hardware: | RevA |  |  |
| OS: | IE8 |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description Albert Burgin 2013-11-06 12:01:48 EST REV 11/5/13 pm-random lockups of data in "real time" monitor This was occurring on a random basis where not when a digital logic state went from high to low but from low to high. The real time data was not changing to reflect changes in the input signal. Some times analysis was dying and sometimes mod buss data was crashing note guardian was still running but not restarting analysis The only was to recover was to reboot the system several times with out the SF6 sensor connected |  |
| --- | --- |

# Bug 108

| Summary: | REV 11/8/13 - SF6 Computed Days to Lockout not being computed |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | Albert Burgin <aburgin@qualitrolcorp.com> |
| Component: | TX28 App | Assignee: | Brian Seiffer <bseiffer@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | cbakhos@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | November 8, 2013 PM |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description Albert Burgin 2013-11-12 14:13:24 EST REV 11/8/13 - SF6 Computed Days to Lockout not being computed After 24 hours of system observation, Computed Days to Lockout is not being calculated. inside story: Steve Mattoon says that Analysis is constantly being stopped and restarted causing the "Computed Days to Lockout" clock to be reset and start over. |  |
| --- | --- |

# Bug 60

| Summary: | REV 11/2/13 - Battery Voltage not correct |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | Albert Burgin <aburgin@qualitrolcorp.com> |
| Component: | TX28 App | Assignee: | Brian Seiffer <bseiffer@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | major | CC: | cbakhos@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description Albert Burgin 2013-11-04 10:04:28 EST Input battery voltage is set to 10 volts DC the real time monitor (analog inputs)say Station Battery -6.321806 Volts It should say +10 volts |  |
| --- | --- |

# Bug 88

| Summary: | REV 11/5/13 pm- SF6 data is being read but not captured correctly |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | Albert Burgin <aburgin@qualitrolcorp.com> |
| Component: | TX28 App | Assignee: | Brian Seiffer <bseiffer@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | blocker | CC: | cbakhos@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | November 5, 2013, 9pm |  |  |
| Hardware: | RevA |  |  |
| OS: | IE9 |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description Albert Burgin 2013-11-06 13:18:34 EST REV 11/5/13 pm- SF6 data is being read but not captured correctly Bug - SF6 data/graph error a) the SF6 graph doesn't generate until logged events is run (by entering the screen) b) The IPC tree is collecting and reading data, but the XML file and the TXT file logs that Liz reads contain 0's for data The effect is that the only recorded data is erroneously always 0 |  |
| --- | --- |

# Bug 61

| Summary: | REV 11/2/13 - Occasional data errors on "Real Time Monitor" screen (Analog and Digital) |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | Albert Burgin <aburgin@qualitrolcorp.com> |
| Component: | TX28 App | Assignee: | Brian Seiffer <bseiffer@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | major | CC: | cbakhos@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description Albert Burgin 2013-11-04 11:31:58 EST Occasionally when pressing the "refresh" button, All Analog and Digital Values are "-1" This occurs approx 1 out of every 10 refreshes. This has been seen more often during Analog parameter change/save/reboot operations (approx 1 out of every 5 times) |  |
| --- | --- |

# Bug 89

| Summary: | REV 11/5/13 pm-SF6 Gas Density chart on home status page is not displayed |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | Albert Burgin <aburgin@qualitrolcorp.com> |
| Component: | TX28 App | Assignee: | Brian Seiffer <bseiffer@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | cbakhos@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | November 5, 2013, 9pm |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description Albert Burgin 2013-11-06 13:35:39 EST REV 11/5/13 pm-SF6 Gas Density chart on home status page is not displayed The display on the home page is blank |  |
| --- | --- |

# Bug 62

| Summary: | REV 11/2/13 - Analog Phase currents are 5000-8000 amps when inputs are turned off(trip) |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | Albert Burgin <aburgin@qualitrolcorp.com> |
| Component: | TX28 App | Assignee: | Brian Seiffer <bseiffer@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | major | CC: | cbakhos@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description Albert Burgin 2013-11-04 11:43:31 EST In the real time monitor screen Analog Phase currents indicate a residual current reading of 5000-8000 amps when inputs are turned off(trip)or a trip event occurs AC rms noise at input measures to be 2mv ac rms CT set to 240000:1 Note additional test: input phase A current shorted at input(shunt) residual current still reads 900 to 6000 amps when it should read 0 |  |
| --- | --- |

# Bug 127

| Summary: | REV 11/15/13 - BCM lockups |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | Albert Burgin <aburgin@qualitrolcorp.com> |
| Component: | TX28 App | Assignee: | Brian Seiffer <bseiffer@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | critical | CC: | aburgin@qualitrolcorp.com, cbakhos@qualitrolcorp.com |
| Priority: | High |  |  |
| Version: | November 15, 2013 PM |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description Albert Burgin 2013-11-18 12:40:18 EST REV 11/15/13 - BCM lockups BCM Locks up about 1 every couple of hours Board is not exercised - (no trips, no Lockouts) How determined - HTML pages do not respond (SF6 pages)& Tera Term Serial interface not responding Comment 1 Albert Burgin 2013-11-18 13:25:25 EST Updated NOTE: Every time the SF6 menu is accessed, the BCM stops responding and locks up. |  |
| --- | --- |

# Bug 63

| Summary: | REV 11/2/13 - Absolute Settings/Trip and close menu loads bad values |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | Albert Burgin <aburgin@qualitrolcorp.com> |
| Component: | TX28 App | Assignee: | Brian Seiffer <bseiffer@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | cbakhos@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description Albert Burgin 2013-11-04 12:01:45 EST While trying to set I2T values and pressing save error in save operation indicating illegal values - Values highlighted for errors are overtravel, rebound and velocity Note: for Overtravel: Rebound: & Velocity: default loaded values are real numbers. Input field only wants integers observed effect - will not allow save. This may be an HTML issue!!!!!! One idea- leave these blocks blank and let customer put in what ever they want. |  |
| --- | --- |

# Bug 64

| Summary: | REV 11/2/13 - Stored Events - Breaker shot records not being captured |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | Albert Burgin <aburgin@qualitrolcorp.com> |
| Component: | TX28 App | Assignee: | Brian Seiffer <bseiffer@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | blocker | CC: | cbakhos@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description Albert Burgin 2013-11-04 12:09:12 EST Under stored events, breaker short records are not being captured. trips and closes are not recorded |  |
| --- | --- |

# Bug 65

| Summary: | rev 11/4/13 - Menu item, in SF6, RS485 option non functional |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | Albert Burgin <aburgin@qualitrolcorp.com> |
| Component: | TX28 App | Assignee: | Brian Seiffer <bseiffer@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | minor | CC: | cbakhos@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | V1.01.00 |  |  |
| Hardware: | RevA |  |  |
| OS: | IE8 |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description Albert Burgin 2013-11-04 15:12:44 EST Menu item, in SF6, RS485 option non functional Under Configure Analog Inputs > sf6 channel/temperature the option to enable RS485 under SF6 input device doesn't function |  |
| --- | --- |

# Bug 94

| Summary: | REV 11/8/13 - Input checks voltage error |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | Albert Burgin <aburgin@qualitrolcorp.com> |
| Component: | TX28 App | Assignee: | Brian Seiffer <bseiffer@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | major | CC: | aburgin@qualitrolcorp.com, cbakhos@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | November 8, 2013 PM |  |  |
| Hardware: | RevA |  |  |
| OS: | FireFox (Mozilla) |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description Albert Burgin 2013-11-11 10:21:51 EST Maintenance > Input Checks Voltage A is still listed as 23489 with no voltage present Comment 1 Albert Burgin 2013-11-11 12:42:53 EST Per Carole 94- on hold- voltage not supported for this release |  |
| --- | --- |

# Bug 66

| Summary: | rev 11/4/13 PM - Real time monitor screen values = 0 or -1 |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | Albert Burgin <aburgin@qualitrolcorp.com> |
| Component: | TX28 App | Assignee: | Brian Seiffer <bseiffer@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | major | CC: | cbakhos@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | V1.02.00 (11/4/13 pm) |  |  |
| Hardware: | RevA |  |  |
| OS: | IE8 |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description Albert Burgin 2013-11-04 18:39:54 EST Noticed: It appears when the guardian process is killed off in firmware, the menu data reported in the real time Monitor screen all go to either 0 or -1 |  |
| --- | --- |

# Bug 95

| Summary: | REV 11/8/13 - clock error |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | Albert Burgin <aburgin@qualitrolcorp.com> |
| Component: | TX28 App | Assignee: | Brian Seiffer <bseiffer@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | minor | CC: | cbakhos@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | November 8, 2013 PM |  |  |
| Hardware: | RevA |  |  |
| OS: | FireFox (Mozilla) |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description Albert Burgin 2013-11-11 10:22:44 EST Maintenance > Info system time is incorrect |  |
| --- | --- |

# Bug 67

| Summary: | rev 11/4/13 PM - Status LED's not indicating warnings |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | Albert Burgin <aburgin@qualitrolcorp.com> |
| Component: | TX28 App | Assignee: | Brian Seiffer <bseiffer@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | major | CC: | cbakhos@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | V1.02.00 (11/4/13 pm) |  |  |
| Hardware: | RevA |  |  |
| OS: | IE8 |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description Albert Burgin 2013-11-04 18:44:14 EST SF6 pressure is at the low end of the yellow zone and the SF6 LED warning is not on |  |
| --- | --- |

# Bug 97

| Summary: | REV 11/8/13 - Real Time Station Battery measurement is about 12 volts low in measurement |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | Albert Burgin <aburgin@qualitrolcorp.com> |
| Component: | TX28 App | Assignee: | Brian Seiffer <bseiffer@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | major | CC: | aburgin@qualitrolcorp.com, cbakhos@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | November 8, 2013 PM |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description Albert Burgin 2013-11-11 10:25:24 EST Events and Records > Real Time Monitor Station Battery measurement is about 12 volts low in measurement Comment 1 Albert Burgin 2013-11-11 12:47:49 EST Per Carole 97- hold- requires calibration |  |
| --- | --- |

# Bug 68

| Summary: | REV 11/4/13 PM - I2T values are not accumulating |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | Albert Burgin <aburgin@qualitrolcorp.com> |
| Component: | TX28 App | Assignee: | Brian Seiffer <bseiffer@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | critical | CC: | cbakhos@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | V1.02.00 (11/4/13 pm) |  |  |
| Hardware: | RevA |  |  |
| OS: | IE8 |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description Albert Burgin 2013-11-04 18:46:23 EST REV 11/4/13 PM - I2T values are not accumulating with breaker trips and closures screen: System> home status |  |
| --- | --- |

# Bug 100

| Summary: | REV 11/8/13 - configure breaker settings is still not functional |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | Albert Burgin <aburgin@qualitrolcorp.com> |
| Component: | TX28 App | Assignee: | Brian Seiffer <bseiffer@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | blocker | CC: | aburgin@qualitrolcorp.com, cbakhos@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | November 8, 2013 PM |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description Albert Burgin 2013-11-11 10:31:38 EST REV 11/8/13 - configure breaker settings is still not functional configure breaker settings > operation settings is still not functional Comment 1 Albert Burgin 2013-11-11 12:49:14 EST Per Carole 100- hold- ops setting not supported for this release |  |
| --- | --- |

# Bug 70

| Summary: | REV 11/4/13 PM - System events log filling up with data |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | Albert Burgin <aburgin@qualitrolcorp.com> |
| Component: | TX28 App | Assignee: | Brian Seiffer <bseiffer@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | major | CC: | cbakhos@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | V1.02.00 (11/4/13 pm) |  |  |
| Hardware: | RevA |  |  |
| OS: | IE8 |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description Albert Burgin 2013-11-04 19:06:55 EST Menu: Events and Records > Logged Events the System Events log is filling up with unknown record type events at sometimes 3-4 per second There are 1158 records so far. I can see the need for a clear records button |  |
| --- | --- |

# Bug 55

| Summary: | Rev 3 BUG - Heater 1 input Digital) |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | Albert Burgin <aburgin@qualitrolcorp.com> |
| Component: | TX28 App | Assignee: | Brian Seiffer <bseiffer@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | major | CC: | cbakhos@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description Albert Burgin 2013-11-01 10:30:38 EDT The BCM doesn't seem to react badly to most digital inputs, however, the Heater 1 Input causes a lot of triggers - It is handles different than the other digital inputs. Observed effect: Causes an instability in the HTML pages where the outputs change between no inputs/ all digital inputs high, no analog signals and / the correct signals (minus scaling) scaling is a separate issue. |  |
| --- | --- |

# Bug 145

| Summary: | Updating xml files (esp. analysis.xml) can cause break in notification |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | Brian Seiffer <bseiffer@qualitrolcorp.com> |
| Component: | TX28 App | Assignee: | Brian Seiffer <bseiffer@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | cbakhos@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | Linux |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description Brian Seiffer 2013-12-05 11:05:16 EST Occassional (difficult to reproduce..) bug is notice after rebooting system after updating apps and their XML files. Especially noticed with updates to analysis.xml. Symptom is that on reboot - among other things not working, manual trigger button will not cause a breaker shot recording to occur. I believe the issue is with the IPCS callback/notification feature. The workaround is to reboot the system two more times. notifications appear to be returned to a functioning state (until the next time the xml file(s) are updated). |  |
| --- | --- |

# Bug 71

| Summary: | REV 11/4/13 PM - BCM shot records are blank |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | Albert Burgin <aburgin@qualitrolcorp.com> |
| Component: | TX28 App | Assignee: | Brian Seiffer <bseiffer@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | major | CC: | cbakhos@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | V1.02.00 (11/4/13 pm) |  |  |
| Hardware: | RevA |  |  |
| OS: | IE8 |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description Albert Burgin 2013-11-04 19:09:41 EST Menu: Events and Records> Stored Records - in the display of Breaker Shot Records, in opening up the records, the records are all 0's |  |
| --- | --- |

# Bug 69

| Summary: | REV 11/4/13 PM - Spare input to BCM non-functional |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | Albert Burgin <aburgin@qualitrolcorp.com> |
| Component: | Hardware | Assignee: | Carole Bakhos <cbakhos@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | major | CC: | cbakhos@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | V1.02.00 (11/4/13 pm) |  |  |
| Hardware: | RevA |  |  |
| OS: | IE8 |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description Albert Burgin 2013-11-04 18:48:36 EST Spare input to BCM is not recognizing a 80- volt DC input in TB2, pins 9 & 10 |  |
| --- | --- |

# Bug 162

| Summary: | No units displayed for the values associated with "A", "B" and "C" on the Accumulated I2t Breaker Status Graph. |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | HTML | Assignee: | Carole Bakhos <cbakhos@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | cbakhos@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-12-14 09:48:42 EST No units displayed for the values associated with "A", "B" and "C" on the Accumulated I2t Breaker Status Graph. There are very large numbers for the values of A, B and C. No identifiers for A, B and C (Breakers), nor are there units on the huge numbers, i.e. A:74725933 B:72356468 C:75823137 |  |
| --- | --- |

# Bug 146

| Summary: | ADC-15 value is displaying values around -133200 volts with no input connected. |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | HTML | Assignee: | Carole Bakhos <cbakhos@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | cbakhos@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-12-13 15:01:30 EST ADC-15 value is displaying values around -133200 volts with no input connected. This value is displayed in the real time monitor of the web page. The name is set to Station battery. |  |
| --- | --- |

# Bug 163

| Summary: | Category Title "Stored Records" should be renamed to "Breaker Shot Records" in the Events and Records tree of the navigation bar. |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | HTML | Assignee: | Carole Bakhos <cbakhos@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | cbakhos@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-12-14 09:51:37 EST Category Title "Stored Records" should be renamed to "Breaker Shot Records" in the Events and Records tree of the navigation bar. |  |
| --- | --- |

# Bug 104

| Summary: | REV 11/8/13 - LED's stayed on after breaker trip and later close. |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | Albert Burgin <aburgin@qualitrolcorp.com> |
| Component: | HTML | Assignee: | Carole Bakhos <cbakhos@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | major | CC: | bseiffer@qualitrolcorp.com, cbakhos@qualitrolcorp.com |
| Priority: | High |  |  |
| Version: | November 8, 2013 PM |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description Albert Burgin 2013-11-11 16:39:26 EST REV 11/8/13 - LED's stayed on after breaker trip and later close. Menu: System > Home/Status Breaker Status and Breaker Warning indicators turned "yellow" and "red" and never turned off. Conditions of test: This AM when the power was turned on to the BCM board, the "Breaker Status" and "Breaker Warning" indicators were both a neutral "White" in color. When a trip was initiated, the "Breaker Warning" indicator turned yellow and the "Breaker Status" indicator turned red. When the Breaker was re-closed (about 2-3 minutes later)the indicators remained on and have stayed on for 6 hours. They have not reset to the neutral white color. |  |
| --- | --- |

# Bug 148

| Summary: | help link doesn't work |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | HTML | Assignee: | Carole Bakhos <cbakhos@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | cbakhos@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-12-13 16:12:50 EST click help and nothing happens. |  |
| --- | --- |

# Bug 165

| Summary: | "No fields were changed. Save aborted." message after checking all of the checkboxes at the bottom of the Analysis Parameters page. |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | HTML | Assignee: | Carole Bakhos <cbakhos@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | cbakhos@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-12-14 10:10:33 EST "No fields were changed. Save aborted." message after checking all of the checkboxes at the bottom of the Analysis Parameters page. checked all of the checkboxes in the Contact Duty Preset section of the page and clicked the Save button. The error message was displayed and nothing was Saved or changed. |  |
| --- | --- |

# Bug 149

| Summary: | release notes link does not display release notes. |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | HTML | Assignee: | Carole Bakhos <cbakhos@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | cbakhos@qualitrolcorp.com, dplatten@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-12-13 16:15:14 EST release notes link does not display release notes. |  |
| --- | --- |

# Bug 166

| Summary: | Breaker Shot Record not created after clicking the Manual Trigger button on the Maintenance - Info page. |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | HTML | Assignee: | Carole Bakhos <cbakhos@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | cbakhos@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-12-14 10:16:17 EST Breaker Shot Record not created after clicking the Manual Trigger button on the Maintenance - Info page. |  |
| --- | --- |

# Bug 167

| Summary: | Maintenance - Finger Prints page not operational |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | HTML | Assignee: | Carole Bakhos <cbakhos@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | cbakhos@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-12-14 10:21:11 EST Maintenance - Finger Prints page not operational |  |
| --- | --- |

# Bug 153

| Summary: | Phase B and Phase C motor currents are disabled and not available to be enabled. |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | HTML | Assignee: | Carole Bakhos <cbakhos@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | cbakhos@qualitrolcorp.com, dplatten@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-12-13 16:32:13 EST Phase B and Phase C motor currents are disabled and not available to be enabled. suggest hiding them if they aren't meant to be used now. |  |
| --- | --- |

# Bug 154

| Summary: | Phase B and Phase C travel transducers on the Travel page are disabled and not available. |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | HTML | Assignee: | Carole Bakhos <cbakhos@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | cbakhos@qualitrolcorp.com, dplatten@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-12-13 16:34:58 EST Phase B and Phase C travel transducers on the Travel page are disabled and not available. suggest to hide them if not intended to be used now. page http://10.75.24.36/ana_travel.html |  |
| --- | --- |

# Bug 155

| Summary: | All buttons on BCM Configuration Files page are disabled; checkboxes can be checked in the table below. |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | HTML | Assignee: | Carole Bakhos <cbakhos@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | cbakhos@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-12-13 16:56:07 EST All buttons on BCM Configuration Files page are disabled; checkboxes can be checked in the table below. This functionality is quite important but if it is not intended to work now the whole page should be disabled, not just the buttons because it feels like the buttons should be enabled after selecting files from the table. |  |
| --- | --- |

# Bug 171

| Summary: | SF6 alarm condition is toggling back and forth to normal state. |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | HTML | Assignee: | Carole Bakhos <cbakhos@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | cbakhos@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-12-14 16:13:38 EST SF6 alarm condition is toggling back and forth to normal state. System Event Logs Timestamp Item # Type Type Definition Timestamp Item # Type Type Definition 14/12/2013 15:59:26 132 4176 SF6 Lockout condition cleared 14/12/2013 15:59:21 131 3884 SF6 Pressure Limit Warning 14/12/2013 15:59:16 130 4176 SF6 Lockout condition cleared 14/12/2013 15:59:11 129 3884 SF6 Pressure Limit Warning 14/12/2013 15:59:06 128 4176 SF6 Lockout condition cleared 14/12/2013 15:59:01 127 3884 SF6 Pressure Limit Warning 14/12/2013 15:58:56 126 4176 SF6 Lockout condition cleared 14/12/2013 15:58:51 125 3884 SF6 Pressure Limit Warning 14/12/2013 15:58:46 124 4176 SF6 Lockout condition cleared 14/12/2013 15:58:41 123 3884 SF6 Pressure Limit Warning 14/12/2013 15:58:36 122 4176 SF6 Lockout condition cleared 14/12/2013 15:58:31 121 3884 SF6 Pressure Limit Warning 14/12/2013 15:58:26 120 4176 SF6 Lockout condition cleared 14/12/2013 15:58:21 119 3884 SF6 Pressure Limit Warning 14/12/2013 15:58:16 118 4176 SF6 Lockout condition cleared 14/12/2013 15:58:11 117 3884 SF6 Pressure Limit Warning 14/12/2013 15:58:06 116 4176 SF6 Lockout condition cleared 14/12/2013 15:58:01 115 3884 SF6 Pressure Limit Warning 14/12/2013 15:57:56 114 4176 SF6 Lockout condition cleared 14/12/2013 15:57:51 113 3884 SF6 Pressure Limit Warning 14/12/2013 15:57:46 112 4176 SF6 Lockout condition cleared |  |
| --- | --- |

# Bug 173

| Summary: | Breaker Shot Record file timestamp does not format single seconds correctly. |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | HTML | Assignee: | Carole Bakhos <cbakhos@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | cbakhos@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-12-15 21:20:49 EST Breaker Shot Record file timestamp does not format single seconds correctly. i.e. 2 should have a preceding zero. 08:09:2 |  |
| --- | --- |

# Bug 160

| Summary: | System events log is not cleared after using the "Clear All" button with the description "All Records and Logs". |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | HTML | Assignee: | Carole Bakhos <cbakhos@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | cbakhos@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-12-13 18:27:14 EST System events log is not cleared after using the "Clear All" button with the description "All Records and Logs". expected all records and logs to be cleared. |  |
| --- | --- |

# Bug 161

| Summary: | Timestamp format incorrect for the SF6 log. |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | HTML | Assignee: | Carole Bakhos <cbakhos@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | cbakhos@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-12-13 18:48:08 EST Timestamp format incorrect for the SF6 log. The other logs in the same table are suspect as well, regarding this issue. date format is displayed as day month year instead of the expected month day year. i.e. 13/12/2013 for dec 13 2013. |  |
| --- | --- |

# Bug 126

| Summary: | REV 11/15/13 - Battery Voltage` |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | Albert Burgin <aburgin@qualitrolcorp.com> |
| Component: | TX28 App | Assignee: | Carole Bakhos <cbakhos@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | cbakhos@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | November 15, 2013 PM |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description Albert Burgin 2013-11-18 12:02:10 EST REV 11/15/13 - Events and Records > Real Time Monitor Station Battery measurement is about 12 volts low in measurement. Measured voltage in is 1 |  |
| --- | --- |

# Bug 15

| Summary: | residual noise with 0 volts input |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | Albert Burgin <aburgin@qualitrolcorp.com> |
| Component: | TX28 App | Assignee: | Carole Bakhos <cbakhos@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | cbakhos@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | FireFox (Mozilla) |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description Albert Burgin 2013-10-28 14:37:23 EDT "Screen: Real Time Monitor with breaker open Analog Inputs ADC-1 Phase current A reads 88.048454 volts with 0 volts peak AC ADC-2 Phase current B reads 49.203548 volts with 0 volts peak AC ADC-3 Phase current C reads 54-382866 volts with 0 volts peak AC all phases true readings vary looks like noise" Comment 1 Carole Bakhos 2013-12-14 15:00:46 EST Known HW noise on inputs |  |
| --- | --- |

# Bug 48

| Summary: | Rev 2 bug- Analog inputs for trip and close not functioning |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | Albert Burgin <aburgin@qualitrolcorp.com> |
| Component: | TX28 App | Assignee: | Carole Bakhos <cbakhos@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | critical | CC: | cbakhos@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description Albert Burgin 2013-10-29 15:06:47 EDT Menu: Events and records > real time monitor ADC-9 not registering trip waveform (when elongated to 30 seconds) ADC-12 not registering Close waveform (when elongated to 30 seconds) |  |
| --- | --- |

# Bug 132

| Summary: | REV 11/15/13 - Voltage A and B is still listed as high numbers |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | Albert Burgin <aburgin@qualitrolcorp.com> |
| Component: | TX28 App | Assignee: | Carole Bakhos <cbakhos@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | cbakhos@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | November 15, 2013 PM |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description Albert Burgin 2013-11-18 12:46:41 EST REV 11/15/13 - Voltage A and B is still listed as high numbers Maintenance > Input Checks Voltage A and B is still listed as high numbers (Voltage A = 22000 while voltage B = -17000 with no voltage present |  |
| --- | --- |

# Bug 51

| Summary: | Rev 2 bug- lockups |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | Albert Burgin <aburgin@qualitrolcorp.com> |
| Component: | TX28 App | Assignee: | Carole Bakhos <cbakhos@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | critical | CC: | cbakhos@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | FireFox (Mozilla) |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description Albert Burgin 2013-10-29 16:18:22 EDT Rev 2 bug- lockups Menu: Configure Analog Inputs > AC Currents Menu: Configure Analog Inputs > Battery Channel changing and saving settings immediately locks up the BCM symptom: no longer recognizes Digital input changes(the part that works) Comment 1 Carole Bakhos 2013-12-14 15:10:19 EST Haven't seen it in a while |  |
| --- | --- |

# Bug 147

| Summary: | SF6 values are not zero when there is no pressure applied to the SF6 sensor. |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | TX28 DMA | Assignee: | Carole Bakhos <cbakhos@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | cbakhos@qualitrolcorp.com, dplatten@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-12-13 15:12:58 EST SF6 values are not zero when there is no pressure applied to the SF6 sensor. 0 psi applied to SF6 sensor. the following values are displayed on the real time monitor of the webpage: 14.6 psia for pressure 6.06 g/L density Comment 1 David Platten 2013-12-13 15:13:23 EST expected values close to zero. |  |
| --- | --- |

# Bug 92

| Summary: | REV 11/8/13 - Real Time Values occasionally error |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | Albert Burgin <aburgin@qualitrolcorp.com> |
| Component: | TX28 App | Assignee: | Derrick Brazil <dbrazil@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | critical | CC: | aburgin@qualitrolcorp.com, cbakhos@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | November 8, 2013 PM |  |  |
| Hardware: | RevA |  |  |
| OS: | FireFox (Mozilla) |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description Albert Burgin 2013-11-11 10:19:27 EST Events and Records > Real Time Monitor Ocassionally all values will go to CT-1 to CT-10: All Digital inputs "ON" and RTU-1,2,3: All SF6 inputs are 0 ADC-16: The temperature is 106 ADC-15: the battery voltage is -0.0056 (additional comments from) From: Deligi, Carlos Sent: Friday, November 08, 2013 5:02 PM To: Winfree, David; Lehmann, Liz; LaFrance, Linda; Bakhos, Carole Cc: Phillip L. Corliss; Irani, Grant; Kulshrestha, Ashish Subject: Some All, Yesterday I got a behavior on the Real Time Monitoring page showing in the following pictures: Breaker Status: Breaker de-energyzed and Heater 1 ON - every page refresh it would show the status of Heater 1 ON and next refresh OFF, and then everything ON. See Pictures attached, this cause a lot confusin. In order to make the heater work I had to give between 6 to 7 cable turns around the Split-core CT to make it work (Heater consume 0.5 Amps and the Split Core CT only act after 3 Amps only. Anyway, the behavior of the page was there with CT on or OFF. |  |
| --- | --- |

# Bug 93

| Summary: | REV 11/8/13 - Input Checks Values occasionally error |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | Albert Burgin <aburgin@qualitrolcorp.com> |
| Component: | TX28 App | Assignee: | Derrick Brazil <dbrazil@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | aburgin@qualitrolcorp.com, cbakhos@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | November 8, 2013 PM |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description Albert Burgin 2013-11-11 10:20:37 EST Maintenance > Input Checks occasionally all analog values go to "-1" while all digital values go to "1" Comment 1 Albert Burgin 2013-11-11 12:41:38 EST This is a different page than 92 - issue is related but not the same |  |
| --- | --- |

# Bug 131

| Summary: | REV 11/15/13 -all analog values go to "-1" |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | Albert Burgin <aburgin@qualitrolcorp.com> |
| Component: | TX28 App | Assignee: | Derrick Brazil <dbrazil@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | cbakhos@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | November 15, 2013 PM |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description Albert Burgin 2013-11-18 12:45:39 EST REV 11/15/13 -all analog values go to "-1" Maintenance > Input Checks occasionally all analog values go to "-1" while all digital values go to "1" |  |
| --- | --- |

# Bug 99

| Summary: | REV 11/8/13 - Home Page LED's |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | Albert Burgin <aburgin@qualitrolcorp.com> |
| Component: | TX28 App | Assignee: | Derrick Brazil <dbrazil@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | critical | CC: | aburgin@qualitrolcorp.com, cbakhos@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | November 8, 2013 PM |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description Albert Burgin 2013-11-11 10:29:38 EST REV 11/8/13 - Home Page LED's The LED display on the home page does not appear to be functional |  |
| --- | --- |

# Bug 14

| Summary: | battery voltage not reading |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | Albert Burgin <aburgin@qualitrolcorp.com> |
| Component: | TX28 App | Assignee: | David Platten <dplatten@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | cbakhos@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | FireFox (Mozilla) |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description Albert Burgin 2013-10-28 14:35:32 EDT "Screen: Real Time Monitor Screen: input check ADC-15 station battery reads 0 volts- actual input set to 1 V dc note: Labview input verified" Comment 1 Carole Bakhos 2013-12-14 14:59:33 EST Retest |  |
| --- | --- |

# Bug 47

| Summary: | Rev 2 bug- Battery voltage not registering |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | Albert Burgin <aburgin@qualitrolcorp.com> |
| Component: | TX28 App | Assignee: | David Platten <dplatten@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | blocker | CC: | cbakhos@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | FireFox (Mozilla) |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description Albert Burgin 2013-10-29 15:05:37 EDT Menu: Events and records > real time monitor ADC-15 not registering battery voltage of up to 5 volts DC (refresh pressed several times) NOTE: Temp (ADC-16) OK |  |
| --- | --- |

# Bug 49

| Summary: | Rev 2 bug- Digital inputs for trip and close are backwards |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | Albert Burgin <aburgin@qualitrolcorp.com> |
| Component: | TX28 App | Assignee: | David Platten <dplatten@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | major | CC: | cbakhos@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description Albert Burgin 2013-10-29 15:09:23 EDT Menu: Events and records > real time monitor Digital inputs for trip and close are backwards DIGITAL INPUTS CT-3 -turns on during open (close input command) CT-1 -turns on during CLOSE (TRIP input command) Labview signals verified correct signals stretched to 30 second duration to catch and verify |  |
| --- | --- |

# Bug 52

| Summary: | Rev 2 BUG - Some channels appear to be not connected |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | Albert Burgin <aburgin@qualitrolcorp.com> |
| Component: | TX28 App | Assignee: | David Platten <dplatten@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | cbakhos@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |
| Attachments: | excel screen shot |  |  |

| Description Albert Burgin 2013-10-30 13:56:49 EDT Rev 2 BUG - Some channels appear to be not connected Screen: Maintenance > Input Checks with breaker status as noted (in attachment) Active Analog Channels - Phase Current A, Phase Cu rent B, Phase Curent C, Trip Coil R, Close Coil R, Station Battery shorted Analog inputs - Voltage A, Voltage B, Motor Return R, Motor Return S, Motor Return T, Trip Coil S, Trip Coil T, Close Coil S, Close Coil T Noted: Previously channels were left floating - Shorting unused channels cleaned up all Noise. Note should be added to field install instructions to short all unused analog channels (See Screen Shot of data captured in excel- if attachment not there, ask and I will send it) Voltage Input A and Motor Current A respond correctly (report near 0 values) Channels "Trip Coil 1", "Trip Coil 2", "Close Coil 1" appear to be not reporting 0 forced input. Values are approx -2700 Note: these channels may not be implemented as of yet, but bug was entered as a reminder placeholder. Comment 1 Albert Burgin 2013-10-30 13:58:33 EDT Created attachment 2 [details] excel screen shot |  |
| --- | --- |

# Bug 130

| Summary: | REV 11/15/13 - I2T is still not accumulating |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | Albert Burgin <aburgin@qualitrolcorp.com> |
| Component: | TX28 App | Assignee: | Keith Manne <kmanne@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | critical | CC: | aburgin@qualitrolcorp.com, cbakhos@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | November 15, 2013 PM |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description Albert Burgin 2013-11-18 12:44:29 EST REV 11/15/13 - I2T is still not accumulating on the home page |  |
| --- | --- |

# Bug 141

| Summary: | REV 11/19/13 - I2T not accumulating for Phase B&C |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | Albert Burgin <aburgin@qualitrolcorp.com> |
| Component: | TX28 App | Assignee: | Keith Manne <kmanne@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | critical | CC: | cbakhos@qualitrolcorp.com |
| Priority: | Highest |  |  |
| Version: | November 19, 2013 PM |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description Albert Burgin 2013-11-19 14:54:21 EST REV 11/19/13 - I2T not accumulating for Phase B&C I2T records is accumulating for Phase A Current, but is not showing up for Phase B Current or Phase C current. after a trip and a close operation |  |
| --- | --- |

# Bug 101

| Summary: | REV 11/8/13 - I2T is still not accumulating on the home page |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | Albert Burgin <aburgin@qualitrolcorp.com> |
| Component: | TX28 App | Assignee: | Keith Manne <kmanne@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | blocker | CC: | aburgin@qualitrolcorp.com, cbakhos@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | November 8, 2013 PM |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description Albert Burgin 2013-11-11 10:32:56 EST REV 11/8/13 - I2T is still not accumulating on the home page |  |
| --- | --- |

# Bug 164

| Summary: | No change seen when checking the "Show Points" or the "Float Y-axis" checkboxes on the SF6 Monitor. |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | HTML | Assignee: | Liz Lehmann <llehmann@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | cbakhos@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-12-14 10:02:09 EST No change seen when checking the "Show Points" or the "Float Y-axis" checkboxes on the SF6 Monitor. expected something to change. |  |
| --- | --- |

# Bug 150

| Summary: | user manual link does not display user manual. |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | HTML | Assignee: | Liz Lehmann <llehmann@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | cbakhos@qualitrolcorp.com, dplatten@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-12-13 16:17:10 EST user manual link does not display user manual. |  |
| --- | --- |

# Bug 109

| Summary: | REV 11/8/13 - There is no security on getting into the BCM system |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | Albert Burgin <aburgin@qualitrolcorp.com> |
| Component: | HTML | Assignee: | Liz Lehmann <llehmann@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | cbakhos@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | November 8, 2013 PM |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description Albert Burgin 2013-11-12 14:30:38 EST REV 11/8/13 - There is no security on getting into the BCM system This was requested by San Diego personnel. They requested password security to access the BCM. User and log in functions are not active. |  |
| --- | --- |

# Bug 151

| Summary: | installation guide link does not display installation guide. |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | HTML | Assignee: | Liz Lehmann <llehmann@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | cbakhos@qualitrolcorp.com, dplatten@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-12-13 16:18:24 EST installation guide link does not display installation guide. |  |
| --- | --- |

# Bug 152

| Summary: | Routing table mask box on the connectivity page is too small to hold the full mask. |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | HTML | Assignee: | Liz Lehmann <llehmann@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | cbakhos@qualitrolcorp.com, dplatten@qualitrolcorp.com |
| Priority: | Low |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-12-13 16:23:30 EST Routing table mask box on the connectivity page is too small to hold the full mask. |  |
| --- | --- |

# Bug 90

| Summary: | REV 11/5/13 pm-SF6 graphs not zooming in |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | Albert Burgin <aburgin@qualitrolcorp.com> |
| Component: | HTML | Assignee: | Liz Lehmann <llehmann@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | critical | CC: | cbakhos@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | November 5, 2013, 9pm |  |  |
| Hardware: | RevA |  |  |
| OS: | IE9 |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description Albert Burgin 2013-11-06 13:39:44 EST REV 11/5/13 pm-SF6 graphs not zooming in side by side the SF6 display in Firefox opens and zooms in fairly quickly In IE, the display takes a very L-O-N-G time to display 2-3 minutes Firefox takes 10-20 seconds(approx) |  |
| --- | --- |

# Bug 170

| Summary: | Home / Status page does not auto-refresh |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | HTML | Assignee: | Liz Lehmann <llehmann@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | cbakhos@qualitrolcorp.com |
| Priority: | High |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-12-14 15:46:04 EST Home / Status page does not auto-refresh Expected: status page to automatically refresh for the current status. |  |
| --- | --- |

# Bug 128

| Summary: | REV 11/15/13 - SF6 Graph is not displaying |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | Albert Burgin <aburgin@qualitrolcorp.com> |
| Component: | HTML | Assignee: | Liz Lehmann <llehmann@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | cbakhos@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | November 15, 2013 PM |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description Albert Burgin 2013-11-18 12:41:21 EST REV 11/15/13 - SF6 Graph is not displaying Menu: SF6 monitor When initiating the page from either by link or by web page refresh, the SF6 monitor graph says What is displayed is "To zoom, select region on graph with mouse or use buttons. Show points Float Y-axis" |  |
| --- | --- |

# Bug 156

| Summary: | The value for Type on the maintenance page overruns the disabled label "User [not avail]" |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | HTML | Assignee: | Liz Lehmann <llehmann@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | cbakhos@qualitrolcorp.com |
| Priority: | Low |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-12-13 17:46:14 EST The value for Type on the maintenance page overruns the disabled label "User [not avail]" |  |
| --- | --- |

# Bug 172

| Summary: | SF6 is incorrectly in the alarm condition. |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | DI PIC | Assignee: | Steven Mattoon <smattoon@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | cbakhos@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-12-14 16:28:53 EST SF6 is incorrectly in the alarm condition. min density is 0 g/L max density is 50 g/L current density is 6.03 g/L (no pressure in) computed days to lockout is 0. |  |
| --- | --- |

# Bug 168

| Summary: | SF6 computed days to lockout is too low for the given slope. |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | HTML | Assignee: | Steven Mattoon <smattoon@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | cbakhos@qualitrolcorp.com |
| Priority: | High |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-12-14 15:13:16 EST SF6 computed days to lockout is too low for the given slope. density values are increasing and the computed days to lockout is currently only 342 days. |  |
| --- | --- |

# Bug 169

| Summary: | SF6 computed days to lockout varies too much for a fairly steady input. |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | HTML | Assignee: | Steven Mattoon <smattoon@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | cbakhos@qualitrolcorp.com |
| Priority: | Highest |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-12-14 15:21:38 EST SF6 computed days to lockout varies too much for a fairly steady input. 14/12/2013 15:14:16 14.60 34.61 22.18 0.000 337 NA 14/12/2013 15:14:11 14.60 34.61 22.18 0.000 312 NA 14/12/2013 15:14:06 14.60 34.61 22.18 0.000 347 NA 14/12/2013 15:14:01 14.60 34.61 22.18 0.000 362 NA 14/12/2013 15:13:56 14.60 34.61 22.18 0.000 357 NA 14/12/2013 15:13:51 14.60 34.61 22.18 0.000 357 NA 14/12/2013 15:13:46 14.60 34.61 22.18 0.000 370 NA 14/12/2013 15:13:41 14.60 34.60 22.18 0.000 384 NA 14/12/2013 15:13:36 14.60 34.60 22.18 0.000 409 NA 14/12/2013 15:13:31 14.60 34.61 22.18 0.000 371 NA 14/12/2013 15:13:26 14.60 34.61 22.18 0.000 371 NA 14/12/2013 15:13:21 14.60 34.60 22.18 0.000 432 NA 14/12/2013 15:13:16 14.60 34.60 22.18 0.000 397 NA 14/12/2013 15:13:11 14.60 34.60 22.18 0.000 407 NA lockout is 337, 312, 347, 362 etc... expected: lockout value not to vary at all if the input doesn't change. in this case the density is unchanged at 14.60. |  |
| --- | --- |

# Bug 157

| Summary: | All SF6 logs are not deleted when Clear button used. |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | HTML | Assignee: | Steven Mattoon <smattoon@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | cbakhos@qualitrolcorp.com, dplatten@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-12-13 18:04:43 EST All SF6 logs are not deleted when Clear button used. started with 165 pages of data. After using the SF6 clear log button there are still 95 pages of data. Comment 1 David Platten 2013-12-13 18:07:02 EST update: a few minutes later it looks as if all of the old data has actually been deleted. Maybe all that is needed is a note saying it will take a few minutes or a popup saying when all of the log has been deleted. |  |
| --- | --- |

# Bug 158

| Summary: | Refresh button on SF6 log page does not refresh the log data. |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | HTML | Assignee: | Steven Mattoon <smattoon@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | cbakhos@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-12-13 18:13:52 EST Refresh button on SF6 log page does not refresh the log data. the same data is displayed after a refresh. page is displaying page 1 of 2 and 1 to 25 of 48 items even after refreshing using the button after several minutes with a 5 sec log update time. |  |
| --- | --- |

# Bug 159

| Summary: | Computed days to lockout is incorrect and varying wildly in the SF6 log. |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | David Platten <dplatten@qualitrolcorp.com> |
| Component: | HTML | Assignee: | Steven Mattoon <smattoon@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | normal | CC: | cbakhos@qualitrolcorp.com |
| Priority: | High |  |  |
| Version: | unspecified |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description David Platten 2013-12-13 18:23:56 EST Computed days to lockout is incorrect and varying wildly in the SF6 log. last 10 values for lockout from the log at 5 second intervals: 21245 24273 19648 6415 6415 11843 7204 6049 7458 7458 |  |
| --- | --- |

# Bug 129

| Summary: | REV 11/15/13 - SF6 Computed Days to Lockout not being computed correctly |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | Albert Burgin <aburgin@qualitrolcorp.com> |
| Component: | TX28 App | Assignee: | Steven Mattoon <smattoon@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | major | CC: | cbakhos@qualitrolcorp.com |
| Priority: | Normal |  |  |
| Version: | November 15, 2013 PM |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

| Description Albert Burgin 2013-11-18 12:43:15 EST REV 11/15/13 - SF6 Computed Days to Lockout not being computed correctly With a 50PSI tank and a slow leak set up in a test fixture @8:14 PSI = 50 @9:52 PSI = 42 1:38 = 98 minutes = .0816 PSI per minute = 612 minutes = about 10 hours The SF6 Computed Days to Lockout states 7 days |  |
| --- | --- |

# Bug 142

| Summary: | REV 11/19/13 - Breaker Shot records missing data |  |  |
| --- | --- | --- | --- |
| Product: | Nemo | Reporter: | Albert Burgin <aburgin@qualitrolcorp.com> |
| Component: | TX28 App | Assignee: | Steven Mattoon <smattoon@qualitrolcorp.com> |
| Status: | CONFIRMED --- |  |  |
| Severity: | critical | CC: | cbakhos@qualitrolcorp.com |
| Priority: | High |  |  |
| Version: | November 19, 2013 PM |  |  |
| Hardware: | RevA |  |  |
| OS: | All |  |  |
| Time tracking: | Orig. Est.; Actual Hours; Hours Worked; Hours Left; %Complete; Gain. 0.0; 0.0; 0.0; 0.0; 0; 0.0. |
| Deadline: |  |  |  |

Description Albert Burgin 2013-11-19 15:03:16 EST Seen by Keith and Steve The Breaker shot records are recording a close event 3 times as a Phase A event. ref AC Current I: 0.000 A 0.000 A 0.000 A Duty: 41.80 A2S 0.000 A2S 0.000 A2S Operation overview Op-1 Op-2 Op-3 Phase A: Close Close Close Phase B: NA NA NA Phase C: NA NA NA Operation Counts Phase A: 0 Phase B: 0 Phase C: 0 Other Results Phase A: 887.609 MA2S Phase B: 2 A2S Phase C: 3 A2S Battery Ripple: 0.02242 V Voltage Drop: 0.1625 V High Voltage: 96.13 V Low Voltage: 95.96 V